## Sheet1
ID | Description | Location | Equipment | Type | System | P&ID | Normal Pos | Iso Pos
IV-863A | LIT863A (upper iso) | CRT landing | LIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-863C | LIT863B (upper iso) | CRT landing | LIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-863E | LIT863C (upper iso) | CRT landing | LIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-864A | Level Gauge 864 (upper iso) | CRT landing | LIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-867A | PIT867A iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-867B | PIT867B iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-867C | PIT867C iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-866 | PIT866 iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-868 | PIT868 iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
VCND216 | Condensate Recirc before CV | CRT landing | CV/CRT | Iso Vlv | CND | 20023894-PD-053A | OPEN | CLOSED
VCND132 | Condensate Recirc after CV | CRT landing | CV/CRT | Iso Vlv | CND | 20023894-PD-053A | OPEN | CLOSED
VCND217 | Condensate Recirc CV bypass | CRT landing | CV/CRT | Iso Vlv | CND | 20023894-PD-053A | OPEN | CLOSED
FCV-CND331 | Condensate Recirc CV | CRT landing | CRT | AOCV | CND | 20023894-PD-053A | CLOSED | CLOSED
VCND 378 | Condensate Recirc Vent (after CV) | CRT landing | CRT | Drain/Vent Vlv | CND | 20023894-PD-053A | CLOSED | OPEN
VCND 152 | Condensate Recirc Drain (after CV) | CRT landing | CRT | Drain/Vent Vlv | CND | 20023894-PD-053A | CLOSED | OPEN
VCND 379 | Condensate Recirc Vent (after strainer) | CRT landing | CRT | Drain/Vent Vlv | CND | 20023894-PD-053A | CLOSED | OPEN
VBFW 213 | BFP "A" HP FW recirc vent after strainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 214 | BFP "A" HP FW recirc vent after strainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW | BFP "A" HP FW recirc iso before CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW 218 | BFP "A" HP FW recirc iso after CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW 230 | BFP "B" HP FW recirc vent after strainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 231 | BFP "B" HP FW recirc vent after strainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW | BFP "B" HP FW recirc iso before CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW239 | BFP "B" HP FW recirc iso after CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW 322 | From TCA to CRT vent after srtainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 323 | From TCA to CRT vent after srtainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW | From TCA to CRT before CV iso | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW339 | From TCA to CRT after CV iso | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW 459 | FGPH to receiver tank after strainer vent | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 460 | FGPH to receiver tank after strainer vent | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 379 | FGPH to receiver tank iso after CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VDWS 638 | Normal makeup Iso before and after CV | CRT landing | CRT | Iso Vlv | DWS |  | OPEN | CLOSED
VDWS 639 | Normal makeup Iso before and after CV | CRT landing | CRT | Iso Vlv | DWS |  | OPEN | CLOSED
VDWS 641/642 | Emergency makeup Iso before and after CV | CRT landing | CRT | Iso Vlv | DWS |  | OPEN
VDWS 636 | Makeup CV bypass | CRT landing | CRT | Iso Vlv | DWS |  | CLOSED
VDWS 648 | Normal makeup drain | CRT landing | CRT | Drain/Vent Vlv | DWS |  | CLOSED
VDWS 105 | Normal makeup vent | CRT landing | CRT | Drain/Vent Vlv | DWS |  | CLOSED
VDWS 643 | Emergency makeup drain | CRT landing | CRT | Drain/Vent Vlv | DWS |  | CLOSED
VDWS532F/534F | Emergency makeup FT | CRT landing | FIT | Iso Vlv | DWS |  | OPEN
VDWS528F/530F | Normal makeup FT | CRT landing | FIT | Iso Vlv | DWS |  | OPEN
VAXS174/175 | Steam to air ejector CV iso | CRT landing | CRT/Air ejector | Iso Vlv | AXS |  | OPEN
VAXS153 | Steam to air ejector drain | CRT landing | CRT/Air ejector | Drain/Vent Vlv | AXS |  | CLOSED
VAXS152 | Steam to air ejector CV bypass | CRT landing | CRT/Air ejector | Iso Vlv | AXS |  | CLOSED
VAXS186 | Air ejector PIT iso | CRT landing | PIT | Iso Vlv | AXS |  | OPEN
VAXS183 | Air ejector vent | CRT landing | CRT/Air ejector | Drain/Vent Vlv | AXS |  | CLOSED
| Air ejector suction/discharge | CRT landing | CRT/Air ejector | Iso Vlv | AXS
VAXS168/165 | Sparging steam CV iso | CRT landing | CRT | Iso Vlv | AXS |  | OPEN
VAXS147 | Sparging steam strainer drain | CRT landing | CRT | Drain/Vent Vlv | AXS |  | CLOSED
VAXS182 | Sparging steam strainer vent | CRT landing | CRT | Drain/Vent Vlv | AXS |  | CLOSED
VAXS102/122 | Sparging steam strainer PDIT | CRT landing | CRT | Iso Vlv | AXS |  | OPEN
VAXS145 | Sparging steam CV bypass | CRT landing | CRT | Iso Vlv | AXS |  | CLOSED
VCND106 | ST DT pump discharge Vent | CRT landing | CRT | Drain/Vent Vlv | CND |  | CLOSED
VCND259 | ST DT pump discharge Drain | CRT landing | CRT | Drain/Vent Vlv | CND |  | CLOSED
VCND258 | ST DT pump discharge Vent | CRT landing | CRT | Drain/Vent Vlv | CND |  | CLOSED
VCND | Condensate Receiver Tank drain valve | CRT area | CRT |  | CND |  | CLOSED
VCND | Level indicating instruments (4 lower valves) | CRT area | LIT |  | CND |  | OPEN
| Cond. Receiver Tank PITs | CRT area | PIT |  | CND |  | OPEN
VCND 377 | Condensate Recirc Drain (after strainer) | CRT area | CRT |  | CND |  | CLOSED
VCND 404 | Condensate Recirc Strainer Vent | CRT area | CRT |  | CND |  | CLOSED
VCND 195 | Condensate Recirc Strainer Drain | CRT area | CRT |  | CND |  | CLOSED
VCND 323 | Condensate Recirc Strainer isolation | CRT area | CRT |  | CND |  | OPEN
VCND | Condensate Recirc Strainer DP isolation (2) valves | CRT area | CRT |  | CND |  | OPEN
VCND577 | ACC east loop seal drain | CRT area | ACC |  | CND |  | CLOSED
VCND576 | ACC west loop seal drain | CRT area | ACC |  | CND |  | CLOSED
| ACC street iso bypass trap (2 sets) | CRT area | ACC |  | CND |  | CLOSED
VBFW 381/415 | BFP "A" HP FW recirc drain after strainer | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 215 | BFP "A" HP FW strainer iso | CRT area | Strainer |  | BFW |  | OPEN
VBFW 216/217 | BFP "A" HP FW strainer drain | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 411/412 | BFP "A" HP FW strainer vent | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 232 | BFP "B" HP FW strainer iso | CRT area | Strainer |  | BFW |  | OPEN
VBFW 233/234 | BFP "B" HP FW strainer drain | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 427/428 | BFP "B" HP FW strainer vent | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 338/365 | BFP "B" HP FW recirc drain after strainer | CRT area | CRT |  | BFW |  | CLOSED
VBFW 330/922 | From TCA to Cond. Receiver Tank iso (2) vlvs | CRT area | CRT |  | BFW |  | OPEN
VBFW 165/166 | From TCA to Cond. Receiver Tank drain | CRT area | CRT |  | BFW |  | CLOSED
VBFW 923/532 | From TCA to Cond. Receiver Tank strainer vent | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 333/334 | From TCA to Cond. Receiver Tank strainer drain | CRT area | Strainer |  | BFW |  | CLOSED
VBFW305/306 | From TCA to Cond. Receiver Tank drain after strainer | CRT area | Strainer |  | BFW |  | OPEN
VBFW 290/361 | Gas performance heater to receiver tank iso (2) valves | CRT area |  |  | BFW |  | OPEN
VBFW 402/403 | Gas performance heater to receiver tank drain | CRT area |  |  | BFW |  | CLOSED
VBFW 440/441 | Gas performance heater to receiver tank strainer vent | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 292/366 | Gas performance heater to receiver tank strainer drain | CRT area | Strainer |  | BFW |  | CLOSED
VBFW449/450 | Gas performance heater to receiver tank after strainer drain | CRT area |  |  | BFW |  | CLOSED
VAXS117/201 | Steam trap iso | CRT area |  |  | AXS
VAXS120 | Steam trap bypass | CRT area |  |  | AXS
VAXS119 | Steam trap strainer drain | CRT area |  |  | AXS
VAXS200 | Steam trap drain | CRT area |  |  | AXS
VCND | Inlet valve to strainer #1 | CRT area | CND pump A |  | CND |  | OPEN
VCND | Inlet valve to strainer #2 | CRT area | CND pump A |  | CND |  | CLOSED
VCND | Outlet valve from strainer 1 | CRT area | CND pump A |  | CND |  | OPEN
VCND | Outlet valve from strainer 2 | CRT area | CND pump A |  | CND |  | CLOSED
VCND 166/171 | Strainer Drain valves (2) | CRT area | CND pump A |  | CND |  | CLOSED
VCND 191/320/118/100 | Strainer Vent valves (4) | CRT area | CND pump A |  | CND |  | CLOSED
VCND 179/142 | DP transmitter isolation (2) valves | CRT area | CND pump A |  | CND |  | OPEN
VCND 143 | CND pump suction pressure gauge isolation. | CRT area | CND pump A |  | CND |  | OPEN
VCND 128 | CND Pump Discharge valve | CRT area | CND pump A |  | CND |  | OPEN
VCND 128 | CND Pump Discharge bypass valve | CRT area | CND pump A |  | CND |  | CLOSED
VCND 128 | CND Pump Discharge equalizing valve | CRT area | CND pump A |  | CND |  | OPEN
VCND 818 | Seal supply valve | CRT area | CND pump A |  | CND |  | OPEN
VCND 157/814 | Air vent valve | CRT area | CND pump A |  | CND |  | CLOSED
VCND 820 | Equalizing valve | CRT area | CND pump A |  | CND |  | OPEN
VCND 819 | Seal water pressure gauge | CRT area | CND pump A |  | CND |  | OPEN
VCND 804 | Pump discharge pressure gauge | CRT area | CND pump A |  | CND |  | OPEN
VCND 104 | Pump Discharge pressure transmitter | CRT area | CND pump A |  | CND |  | OPEN
VCND 196 | Pump Discharge Drain | CRT area | CND pump A |  | CND |  | CLOSED
VCND | Inlet valve to strainer 1 | CRT area | CND pump B |  | CND |  | OPEN
VCND | Inlet valve to strainer 2 | CRT area | CND pump B |  | CND |  | CLOSED
VCND | Outlet valve from strainer 1 | CRT area | CND pump B |  | CND |  | OPEN
VCND | Outlet valve from strainer 2 | CRT area | CND pump B |  | CND |  | CLOSED
VCND 361/176 | Strainer Drain valves (2) | CRT area | CND pump B |  | CND |  | CLOSED
154/360/135/129 | Strainer Vent valves (4) | CRT area | CND pump B |  | CND |  | CLOSED
VCND 181/164 | DP transmitter isolation (2) valves | CRT area | CND pump B |  | CND |  | OPEN
VCND 183 | CND pump suction pressure gauge isolation. | CRT area | CND pump B |  | CND |  | OPEN
VCND 194 | CND Pump Discharge valve | CRT area | CND pump B |  | CND
VCND 194 | CND Pump Discharge bypass valve | CRT area | CND pump B |  | CND |  | CLOSED
VCND 194 | CND Pump Discharge equalizing valve | CRT area | CND pump B |  | CND |  | OPEN
VCND 848 | Seal supply valve | CRT area | CND pump B |  | CND |  | OPEN
VCND 333/844 | Air vent valve (2) | CRT area | CND pump B |  | CND |  | CLOSED
VCND 850 | Equalizing valve | CRT area | CND pump B |  | CND |  | OPEN
VCND 846 | Seal water pressure gauge | CRT area | CND pump B |  | CND |  | OPEN
VCND 834 | Pump discharge pressure gauge | CRT area | CND pump B |  | CND |  | OPEN
VCND 137 | Pump Discharge pressure transmitter | CRT area | CND pump B |  | CND |  | OPEN
VCND 167 | Pump Discharge Drain | CRT area | CND pump B |  | CND |  | CLOSED
VCND | Inlet valve to strainer 1 | CRT area | CND pump C |  | CND |  | OPEN
VCND | Inlet valve to strainer 2 | CRT area | CND pump C |  | CND |  | CLOSED
VCND | Outlet valve from strainer 1 | CRT area | CND pump C |  | CND |  | OPEN
VCND | Outlet valve from strainer 2 | CRT area | CND pump C |  | CND |  | CLOSED
VCND 173/178 | Strainer Drain valves (2) | CRT area | CND pump C |  | CND |  | CLOSED
VCND 330/133/168/165 | Strainer Vent valves (4) | CRT area | CND pump C |  | CND |  | CLOSED
VCND 112/192 | DP transmitter isolation (2) valves | CRT area | CND pump C |  | CND |  | OPEN
VCND 131 | CND pump suction pressure gauge isolation. | CRT area | CND pump C |  | CND |  | OPEN
VCND 329 | CND Pump Discharge valve | CRT area | CND pump C |  | CND
VCND 329 | CND Pump Discharge bypass valve | CRT area | CND pump C |  | CND |  | CLOSED
VCND 329 | CND Pump Discharge equalizing valve | CRT area | CND pump C |  | CND |  | OPEN
VCND 878 | Seal supply valve | CRT area | CND pump C |  | CND |  | OPEN
VCND 113/874 | Air vent valve | CRT area | CND pump C |  | CND |  | CLOSED
VCND 880 | Equalizing valve | CRT area | CND pump C |  | CND |  | OPEN
VCND 876 | Seal water pressure gauge | CRT area | CND pump C |  | CND |  | OPEN
VCND 864 | Pump discharge pressure gauge | CRT area | CND pump C |  | CND |  | OPEN
VCND 130 | Pump Discharge pressure transmitter | CRT area | CND pump C |  | CND |  | OPEN
VCND 189 | Pump Discharge Drain | CRT area | CND pump C |  | CND |  | CLOSED
VCND238/236 | Demin Water supply valves | CRT area | CND header |  | CND
VCND 237 | Demin Water drain | CRT area | CND header |  | CND |  | CLOSED
VCND 127 | Common Condensate Discharge Header Vent | CRT area | CND header |  | CND |  | CLOSED
VCND 151 | Common Condensate Discharge Header PIT | CRT area | PIT |  | CND |  | OPEN
VCND 201 | Filter Inlet MOV equalizing valve | CRT area | IRON Filer A |  | CND |  | OPEN
VCND 172 | Filter Outlet | CRT area | IRON Filer A |  | CND |  | OPEN
VCND 172 | Filter Outlet Bypass Valve | CRT area | IRON Filer A |  | CND |  | CLOSED
VCND 172 | Filter Outlet Equalizing Valve | CRT area | IRON Filer A |  | CND |  | OPEN
VCND 139 | Filter Vent | CRT area | IRON Filer A |  | CND |  | CLOSED
VCND 114/144 | Filter Drains (2) | CRT area | IRON Filer A |  | CND |  | CLOSED
VCND 184/177 | Filter D/P Transmitter (2) isolation valves | CRT area | IRON Filer A |  | CND |  | OPEN
VCND 211 | Filter Inlet MOV equalizing valve | CRT area | IRON Filer B |  | CND |  | OPEN
VCND 174 | Filter Outlet | CRT area | IRON Filer B |  | CND |  | OPEN
VCND 174 | Filter Outlet Bypass Valve | CRT area | IRON Filer B |  | CND |  | CLOSED
VCND 174 | Filter Outlet Equalizing Valve | CRT area | IRON Filer B |  | CND |  | OPEN
VCND 140 | Filter Vent | CRT area | IRON Filer B |  | CND |  | CLOSED
VCND 101/362 | Filter Drains (2) | CRT area | IRON Filer B |  | CND |  | CLOSED
VCND 187/180 | Filter D/P Transmitter (2) isolation valves | CRT area | IRON Filer B |  | CND |  | OPEN
VCND 160 | Before MOV isolation valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 160 | Before MOV bypass valve | CRT area | IRON Filter Bypass |  | CND |  | CLOSED
VCND 160 | Before MOV equalizing valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 221 | MOV Equalizing valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 163 | After MOV isolation valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 163 | After MOV equalizing valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 163 | After MOV bypass valve | CRT area | IRON Filter Bypass |  | CND |  | CLOSED
VCND 188 | Iron Filter Bypass line drain | CRT area | IRON Filter Bypass |  | CND |  | CLOSED
VCND | Vent Before Iron Filters | CRT area | IRON Filter Bypass |  | CND |  | CLOSED
VCND272 | Drains tank pumps seal water iso | ST Drains Tank area | ST DT pump |  | CND |  | OPEN
VCND273 | Drains tank pumps seal water drain | ST Drains Tank area | ST DT pump |  | CND |  | CLOSED
| Steam Duct Drip Leg LT iso (6 valves) | ST Drains Tank area | ST DT pump
VSTP 165 | DT pmup A discharge | ST Drains Tank area | ST DT pump |  | VSTP |  | OPEN
VSTP 178 | DT pmup B discharge | ST Drains Tank area | ST DT pump |  | VSTP |  | OPEN
VSTP 166 | DT pump common discharge iso | ST Drains Tank area | ST DT pump |  | VSTP |  | OPEN
| Drains tank sump pump A | ST Drains Tank area | ST DT pump |  | VSTP
| Drains tank sump pump B | ST Drains Tank area | ST DT pump |  | VSTP
VCND 198/367 | HP Drains Tank spray CV iso | ST Drains Tank area | HP DT |  | CND |  | OPEN
VCND 366 | HP Drains Tank spray CV bypass | ST Drains Tank area | HP DT |  | CND |  | CLOSED
VCND 200 | HP Drains Tank spray supply drain | ST Drains Tank area | HP DT |  | CND |  | CLOSED
VSTP 195/196/111/112/134/135 | HP DT Level Transmitters | ST Drains Tank area | LT |  | STP |  | OPEN
VSTP 110 | HP DT PIT | ST Drains Tank area | PT |  | STP |  | OPEN
VSTP 116 | HP DT Drain | ST Drains Tank area | HP DT |  | STP |  | CLOSED
VSTP 113/115 | HP DT Drain to LP DT CV iso | ST Drains Tank area | HP DT |  | STP |  | OPEN
VSTP 370/371 | HP DT Drain to LP DT CV iso | ST Drains Tank area | HP DT |  | STP |  | OPEN
VSTP 114 | HP DT Drain before CV | ST Drains Tank area | HP DT |  | STP |  | CLOSED
VSTP 130 | HP DT Drain before CV | ST Drains Tank area | HP DT |  | STP |  | CLOSED
VSTP 141 | LP DT PIT | ST Drains Tank area | PT |  | STP |  | OPEN
VSTP 143/144/148/149/150/151 | LP DT LT | ST Drains Tank area | LT |  | STP |  | OPEN
VSTP 152 | LP DT drain | ST Drains Tank area | LP DT |  | STP |  | CLOSED
VCND 214/261 | LP Drains Tank spray CV iso | ST Drains Tank area | LP DT |  | STP |  | OPEN
VCND 262 | LP Drains Tank spray CV bypass | ST Drains Tank area | LP DT |  | STP |  | CLOSED
VCND 215 | LP Drains Tank spray supply drain | ST Drains Tank area | LP DT |  | STP |  | CLOSED
VSTP 155/156 | DT pump A suction strainer PDT | ST Drains Tank area | PT |  | STP |  | OPEN
VSTP 118/158 | DT pump A suction drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 117/157 | DT pump A suction vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 161 | DT pmup A vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VCND 279/280 | DT pmup A seal supply | ST Drains Tank area | ST DT pump |  | STP |  | OPEN
VSTP 164 | DT pmup A discharge drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 168/169 | DT pump B suction strainer PDT | ST Drains Tank area | ST DT pump |  | STP |  | OPEN
VSTP 124/171 | DT pump B suction drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 126/170 | DT pump B suction vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 174 | DT pmup B vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VCND 244/245 | DT pmup B seal supply | ST Drains Tank area | ST DT pump |  | STP |  | OPEN
VSTP 177 | DT pmup B discharge drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 386 | DT pump discharge vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 106/258 | DT pump discharge vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 259 | DT pump discharge drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VCND190/175/308/124 | Flow Transmitter (4 valves) | ST upper East | FT |  | CND |  | OPEN
VCND138 | Vent before Gland Steam Condenser | ST upper East | GS condenser |  | CND |  | CLOSED
VCND146 | Local Pressure Gauge | ST upper East | GS condenser |  | CND |  | OPEN
VCND402/403 | Gland Steam Condenser drains (in and out) | ST upper East | GS condenser |  | CND |  | CLOSED
VCND400/401 | Gland Steam Condenser vents (in and out) | ST upper East | GS condenser |  | CND |  | CLOSED
VCND193 | Local Pressure Gauge after GSC | ST upper East | GS condenser |  | CND |  | OPEN
VCND225 | Strainer #1 inlet isolation | ST upper East | Strainer |  | CND |  | OPEN
VCND228 | Strainer #2 inlet isolation | ST upper East | Strainer |  | CND |  | CLOSED
VCND227 | Strainer #1 outlet isolation | ST upper East | Strainer |  | CND |  | OPEN
VCND230 | Strainer #2 outlet isolation | ST upper East | Strainer |  | CND |  | CLOSED
VCND233/234 | Strainer DP isolation valves (2) | ST upper East | Strainer |  | CND |  | OPEN
VCND226/229 | Strainer Drain valves (2) | ST upper East | Strainer |  | CND |  | CLOSED
VCND231/232 | Strainer Vent valves (2) | ST upper East | Strainer |  | CND |  | CLOSED
VCND | Hood Spray and Gland Steam attemperator | ST upper East | Attemperator |  | CND |  | OPEN
VCND271 | Hood spray strainer drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND126/145 | Hood spray FCV isolation valves (2) | ST upper East | Attemperator |  | CND |  | OPEN
VCND147 | Hood spray FCV bypass valve | ST upper East | Attemperator |  | CND |  | CLOSED
VCND123 | Hood spray local gauge | ST upper East | Attemperator |  | CND |  | OPEN
VCND186 | Hood spray vent | ST upper East | Attemperator |  | CND |  | CLOSED
VCND201 | Gland steam attemperator isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND406 | Gland steam attemperator strainer drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND207/209 | Gland steam attemperator flow transmitter (2) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND211 | Gland steam attemperator drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND212 | Gland steam attemperator isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND134 | Curtain spray isolation valve | ST upper East | Attemperator |  | CND |  | OPEN
VCND321/322 | Curtain spray flow transmitter (2) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND324/326 | Curtain spray FCV isolation valves (2) | ST upper East | Attemperator |  | CND |  | OPEN
VCND327 | Curtain spray FCV bypass valve | ST upper East | Attemperator |  | CND |  | CLOSED
VCND328 | Curtain spray PIT | ST upper East | Attemperator |  | CND |  | OPEN
VCND405 | Curtain spray vent | ST upper East | Attemperator |  | CND |  | CLOSED
VCND221 | LP Bypass spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND156/169 | LP Bypass spray flow transmitter (2) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND158 | LP Bypass spray drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND141 | LP Bypass spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND105 | LP Bypass spray drain (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | Attemperator |  | CND |  | CLOSED
VCND223 | CRH ventilator spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND159/162 | CRH ventilator spray Flow transmitter (2) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND108 | CRH ventilator spray drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND109 | CRH ventilator spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND110/216 | CRH ventilator spray vent (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | Attemperator |  | CND |  | CLOSED
VCND363/364 | CRH ventilator spray drain (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | Attemperator |  | CND |  | CLOSED
VCND224 | HRH spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND125/170/301/302 | HRH spray flow transmitter (4) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND116 | HRH spray drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND119 | HRH spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND307 | HRH spray vent | ST upper East | Attemperator |  | CND |  | CLOSED
VCND260 | HRH spray dray (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | Attemperator |  | CND |  | CLOSED
VBFW614/615 | TCA return to Cond.Receiv. Vent | ST upper East | TCA |  | BFW |  | CLOSED
MAW01AA001 | GS Exhauster A inlet | ST upper East | GS condenser |  | STP
MAW01AA002 | GS Exhauster B inlet | ST upper East | GS condenser |  | STP
VSTP 125 | GS Exhauster A outlet | ST upper East | GS condenser |  | STP
VSTP 179 | GS Exhauster B outlet | ST upper East | GS condenser |  | STP
VAXS 196/197/198 | GS supply drain valves | ST upper East | GS condenser |  | STP
VSTP 148/149 | GS supply CV isolations | ST upper East | GS condenser |  | STP
VSTP204 | GS supply CV bypass | ST upper East | GS condenser |  | STP
VSTP105 | HP SV/CV seat drain | ST upper East | ST |  | STP
VSTP107 | HRH SV/CV seat drain AOV iso | ST upper East | ST |  | STP
VCRH 131 | Ventilator CV manual iso. | ST upper East | ST |  | CRH
VCRH 102/103/141/142 | Ventilator line PITs (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | ST |  | CRH
VHRH 113/114 | HRH Bypass warm up line vent | ST upper East | ST |  | HRH
VHRH 116 | HRH Bypass warm up line iso | ST upper East | ST |  | HRH
VHRH 125/126 | HRH Bypass line PITs (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | ST |  | HRH
| Condenser Vacuum PITs (127/128/129) | ST upper East | PT
VCND 501/502/503 | LP turbine exhause pressure PITs | ST upper East | ST |  | CND
01-VAXS 132 | Aux steam header vent (stmr bldg) | ST upper East | Aux Steam Header |  | AXS
01-VAXS 190 | Drain before steam trap | ST upper East | Steam Trap |  | AXS
01-VAXS 191/194 | Steam trap iso | ST upper East | Steam Trap |  | AXS
01-VAXS 202 | Steam Trap bypass | ST upper East | Steam Trap |  | AXS
01-VAXS 195 | Steam Trap strainer drain | ST upper East | Steam Trap |  | AXS
VSTP 119 | GSC drain to funnel | ST lower East | GS condenser |  | STP
VSTP 120/121 | GSC drain isolation before and after trap | ST lower East | GS condenser |  | STP
VSTP 123 | GSC drain trap bypass | ST lower East | GS condenser |  | STP
VSTP 137 | GSC drain trap vent back to GSC | ST lower East | GS condenser |  | STP
VSTP 122 | GSC drain trap strainer drain | ST lower East | GS condenser |  | STP
VSTP 146/147/153/154 | GS Exhauster drains | ST lower East | GS condenser |  | STP
VAX 159 | GS supply iso before superheater | ST lower East | Gland Steam |  | STP
VAXS 101 | GS supply vent before superheater | ST lower East | Gland Steam |  | STP
VAXS 104/105 | GS superheater drain trap | ST lower East | Gland Steam |  | STP
VAXS 107 | GS superheater drain trap bypass | ST lower East | Gland Steam |  | STP
VAXS 106 | GS superheater drain trap strainer drain | ST lower East | Gland Steam |  | STP
VSTP 159/181 | GS mist separator orphis drain | ST lower | Gland Steam |  | STP
VSTP 167 | GS mist separator orphis bypass | ST lower | Gland Steam |  | STP
VSTP 182 | GS mist separator common drain | ST lower | Gland Steam |  | STP
VSTP 131/133 | GS header PT | ST lower | PT |  | STP
VSTP 183/184/185 | GS header drain | ST lower | Gland Steam |  | STP
VSTP 127/129 | GS spill over CV iso | ST lower | Gland Steam |  | STP
VSTP 132 | GS spill over CV bypass | ST lower | Gland Steam |  | STP
VSTP 139/140 | Seals/stem leak off to GSC drain | ST lower | Gland Steam |  | STP
VLPS 142/167 | 2 pressure transmitters (before stop) | ST lower | PT |  | LPS
VLPS 164/152 | Drains on LP steam Bypass line | ST lower East |  |  | LPS
VLPS 101/103/104/106 | Bypass line Drip leg level Isolations | ST lower East |  |  | LPS
VLPS 108/111 | Bypass line Drip leg level drains | ST lower East |  |  | LPS
VLPS 109 | LP steam Bypass drip leg CV isolation | ST lower East |  |  | LPS
| LP steam PIT (turbine side) | ST lower |  |  | LPS
VLPS 163 | LP steam header vent (before drip leg) | ST lower |  |  | LPS
VLPS 169/170/171/172 | LP steam Drip Leg level swithc iso | ST lower |  |  | LPS
VLPS 174/175/176/177 | Vents and drains on level switches | ST lower |  |  | LPS
VLPS 149/150 | Drip leg drans | ST lower |  |  | LPS
VLPS 151 | Drip leg CV iso | ST lower |  |  | LPS
VLPS 173 | LP header vent after strainer | ST lower |  |  | LPS
VLPS | LP steam strainer drain | ST lower |  |  | LPS
VLPS | Manuall iso drain before and after LP steam CV | ST lower |  |  | LPS
MAC03 AA801 | LP Turbine inlet steam PIT (123) | ST lower |  |  | LPS
VHPS 100/101/102/103 | HPS header PITs (outside steamer bldg) | ST lower East |  |  | HPS
VHPS 106/107 | HPS header vent | ST lower East |  |  | HPS
VHPS108 | HPS header Drip Leg manual isolation | ST lower East |  |  | HPS
VHPS109/110 | HPS header Drip Leg drain | ST lower East |  |  | HPS
VSTP104 | HPS after seat drain | ST lower |  |  | HPS
MAA03 AA801/802/803/804/805/806 | HP turbine inlet steam PITs (101/102/103) | ST lower East |  |  | HPS
MAA41 AA801/802/803 | HP turbine exhaust PITs (110/111/112) | ST lower East |  |  | CRH
VCRH 128/143 | HP turbine exhaust PIT | ST lower East |  |  | CRH
VCRH 139/144 | HP turbine exhaust vent | ST lower East |  |  | CRH
VCRH 102/103/141/142 | Ventilator line PITs | ST lower |  |  | CRH
VCRH 108/109/175/177/110/112/176/178 | HP turbine exhaust Drip Leg Level Switches | ST lower East |  |  | CRH
VCRH 101/151/125/150 | HP turbine exhaust Drip Leg Level Switche drains | ST lower East |  |  | CRH
VCRH129/145/126/149 | HP turbine exhaust Drip Leg Level Switche vents | ST lower East |  |  | CRH
VCRH 127 | HP turbine exhaust Drip Leg AOV iso | ST lower East |  |  | CRH
VCRH 133/134 | CRH Drip Leg drain | ST lower East |  |  | CRH
VCRH 104/105/106/107/154/155/156/157 | CRH Drip Leg Level Switches | ST lower East |  |  | CRH
VCRH158/160/161/123 | CRH Drip Leg Level Switche drains | ST lower East |  |  | CRH
VCRH 152/116/153/113 | CRH Drip Leg Level Switche vents | ST lower East |  |  | CRH
VCRH 130 | CRH Drip Leg AOV iso | ST lower East |  |  | CRH
VCRH 135/138 | CRH Drip Leg drain | ST lower East |  |  | CRH
VHRH 115 | HRH Bypass warm up line iso (overhead) | ST lower East |  |  | HRH
VHRH 111/105 | HRH Bypass warm up line vent | ST lower East |  |  | HRH
VHRH 110 | HRH dripleg before SV/CV AOV iso | ST lower East |  |  | HRH
VHRH 120/137 | HRH dripleg drain | ST lower East |  |  | HRH
VSTP106 | HRH after seat drain AOV iso | ST lower East |  |  | HRH
VHRH 100/102/103/104/121/106 | HRH PITs (before stop) | ST lower East |  |  | HRH
MAB03 BR801/802/803 | IP Turbine Inlet steam PITs (113/114/115) | ST lower East |  |  | HRH
VHHS 803/804/805/806/807/808/809/810 | 1st stage HP superheater Drip leg 2 Lvl switches (8) isolation valves | HRSG lower East |  |  | HHS
VHHS 867/868 | 1st stage HP superheater Drip leg drain (2) valves | HRSG lower East |  |  | HHS
VHHS 811/812 | HP Superheater vent to atmoshpere | HRSG lower East |  |  | HHS
VHHS 909/910 | 3rd stage HP superheater Drip leg drain (2) valves | HRSG lower East |  |  | HHS
VHRS 969/970 | Reheater interstage Dripleg drain | HRSG lower West |  |  | HRS
VHIS 856/857 | IP superheater outlet dripleg drain | HRSG lower |  |  | HIS
VHIS 987/988 | IP superheater outlet PIT | HRSG lower |  |  | HIS
VHIS 864/865/866/867/994/995/996/997 | IP steam flow meter | HRSG lower |  |  | HIS
VHIS 801/802 | IP superheater outlet drain (before MOV) | HRSG lower |  |  | HIS
VHIS 908 | IP superheater outlet MOV bypass | HRSG lower |  |  | HIS
VHIS 858/859 | IP steam Header drain (after MOV) | HRSG lower |  |  | HIS
VHLS 811/812/813/814/815/816 | 3 PIT (6) iso valves | HRSG lower West |  |  | HLS
VHLS 808/809 | Sampling | HRSG lower West |  |  | HLS
VHLS 986/987 | Drip leg drain before MOV | HRSG lower West |  |  | HLS
01-VAXS 189/290 | Steam to HP Evap Steam trap ISOs | HRSG lower |  |  | AXS
01-VAXS 289 | Steam to HP Evap Steam trap bypass | HRSG lower |  |  | AXS
01-VAXS 144 | Steam to HP Evap Steam trap strainer drain | HRSG lower |  |  | AXS
01-VAXS 291 | Steam to HP Evap drain before steam trap | HRSG lower |  |  | AXS
VHHS 904 | Steam to HP Evap MOV bypass | HRSG lower |  |  | HHS
VHHS 994/995 | Steam to HP Evap drain after MOV | HRSG lower |  |  | HHS
VHHS 996/997 | Steam to HP Evap strainer drain | HRSG lower |  |  | HHS
01-VHIS 852/853 | Steam to IP Evap strainer drain | HRSG lower |  |  | HIS
01-VHLS 904 | Steam to LP Evap MOV bypass | HRSG lower |  |  | HLS
01-VHLS 985/999 | Steam to LP Evap drain after MOV | HRSG lower |  |  | HLS
01-VHLS 992/993 | Steam to LP Evap strainer drain | HRSG lower |  |  | HLS
01-VAXS 135/136 | Steam to LP Evap Steam trap iso | HRSG lower |  |  | AXS
01-VAXS 138 | Steam to LP Evap Steam trap bypass | HRSG lower |  |  | AXS
01-VAXS 137 | Steam to LP Evap Steam trap strainer drain | HRSG lower |  |  | AXS
01-VAXS 113 | Steam to LP Evap Drain before Steam trap | HRSG lower |  |  | AXS
01-VAXS 155 | Drain before steam trap | HRSG lower NE |  |  | AXS
01-VAXS 112/115 | Steam trap iso | HRSG lower NE |  |  | AXS
01-VAXS 129 | Steam Trap bypass | HRSG lower NE |  |  | AXS
01-VAXS 116 | Steam Trap strainer drain | HRSG lower NE |  |  | AXS
01-VAXS 130 | Drain before steam trap | HRSG lower East |  |  | AXS
01-VAXS 103/161 | Steam trap iso | HRSG lower East |  |  | AXS
01-VAXS 164 | Steam Trap bypass | HRSG lower East |  |  | AXS
01-VAXS 160 | Steam Trap strainer drain | HRSG lower East |  |  | AXS
01-VAXS 199 | Drain before steam trap | HRSG lower West |  |  | AXS
01-VAXS 166/118 | Steam trap iso | HRSG lower West |  |  | AXS
01-VAXS 167 | Steam Trap bypass | HRSG lower West |  |  | AXS
01-VAXS 203 | Steam Trap strainer drain | HRSG lower West |  |  | AXS
VHHS 916/917 | HP FW to economizer PIT (before LCV) |  |  |  | BFW HP |  | OPEN
VHHS 907 | HP drum LCV bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS 901 | HP drum High flow LCV iso | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS | HP drum High flow LCV iso bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | HP drum High flow LCV iso equalizing valve | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 903 | HP drum Low flow LCV iso | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS | HP drum Low flow LCV iso bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | HP drum Low flow LCV iso equalizing valve | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 857/856 | HP drum High flow drain | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS 859/858 | HP drum Low flow drain | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS 902 | HP drum High flow LCV outlet iso | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS | HP drum High flow LCV outlet iso bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | HP drum High flow LCV outlet iso equalizing | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 904 | HP drum Low flow LCV outlet iso | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS | HP drum Low flow LCV outlet iso bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | HP drum Low flow LCV outlet iso equalizing | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 913/912 | HP drum FW drain before MOV | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | MOV 901 bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | MOV 901 equalizing | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 914/915 | HP economizer inlet PIT (after LCV) | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 961/929/930/931/932/933/934/935/936/937 | HP economizer drain root valves | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS 900/906/938/905 | HP economizer drain block valves | HRSG lower West |  |  | BFW HP |  | CLOSED
VBFW 303/304 | FW to TCA drain before cooler | HRSG lower West |  |  | BFW HP |  | CLOSED
VBFW 700/701/929/928 | PDI across TCA | HRSG lower West |  |  | BFW HP |  | OPEN
VBFW 305/294 | Drain After TCA coller | HRSG lower West |  |  | BFW HP |  | CLOSED
VHIS 901 | IP Economizer Inlet Isolation | HRSG lower |  |  | BFW IP
VHIS 901 | IP Economizer Inlet Isolation bypass | HRSG lower |  |  | BFW IP
VHIS 901 | IP Economizer Inlet Isolation equalizing valve | HRSG lower |  |  | BFW IP
VHIS 919/920 | IP Economizer inlet drain valves (2) | HRSG lower |  |  | BFW IP
VHIS | IP Economizer inlet MOV bypass | HRSG lower |  |  | BFW IP
VHIS | IP Economizer inlet MOV equalizing valve | HRSG lower |  |  | BFW IP
VHIS 904 | IP fill line isolation | HRSG lower |  |  | BFW IP
VHIS 906/907 | IP Economizer Inlet PIT isolation (2) valves | HRSG lower |  |  | BFW IP
VHIS 910/911/912 | IP Economizer Drains (Root) | HRSG lower |  |  | BFW IP
VHIS 913 | IP Economizer Drain (Block) | HRSG lower |  |  | BFW IP
VBFW 918/919/820/821/822/823/824/825 | (2) Flow transmitters (8) valves |  |  |  | BFW IP |  | OPEN
VBFW 960/961 | Drain before CV |  |  |  | BFW IP |  | CLOSED
VBFW 848/849 | Strainer Drain (2) valves |  |  |  | BFW IP |  | CLOSED
VBFW 826/827/828/829 | Strainer DPT (4) valves |  |  |  | BFW IP |  | OPEN
VBFW 930 | After CV iso |  |  |  | BFW IP |  | OPEN
VBFW 962/963 | Drain after check (2) valves |  |  |  | BFW IP |  | CLOSED
VBFW 394F/159F/160F | BFP "A" suction PIT iso (3) (at the pump) | HRSG lower West |  |  | BFW |  | OPEN
| BFP "A" CCW inlet/outlet | HRSG lower West |  |  | BFW
VBFW 180F/179F/395F | BFP "B" suction PIT iso (3) | HRSG lower West |  |  | BFW |  | OPEN
| BFP "B" CCW inlet/outlet | HRSG lower West |  |  | BFW
VCND336/375 | Condensate header pressure transmitters | HRSG lower NW |  |  | CND |  | OPEN
VCND103 | Condensate Dump isolation | HRSG lower NW |  |  | CND |  | CLOSED
VCND153 | Drain before condensate dump CV | HRSG lower NW |  |  | CND |  | CLOSED
VCND337/338 | LP economizer pressure transmitters | HRSG lower NW |  |  | CND |  | OPEN
VHLS902/903 | Drain before LP Economizer inlet MOV | HRSG lower NW |  |  | CND |  | CLOSED
VHLS | MOV bypass | HRSG lower NW |  |  | CND |  | CLOSED
VHLS803/804 | Pressure Transmitter isolations | HRSG lower NW |  |  | CND |  | OPEN
VHLS904 | Cold Condensate inlet isolation | HRSG lower NE |  |  | CND |  | OPEN
VHLS907 | Cold Condensate outlet isolation | HRSG lower NE |  |  | CND |  | OPEN
VHLS905 | Hot Condensate inlet isolation | HRSG lower NE |  |  | CND |  | OPEN
VHLS908 | Hot Condensate outlet isolation | HRSG lower NE |  |  | CND |  | OPEN
VHLS909 | Cold Condensate bypass around heat exchanger | HRSG lower NE |  |  | CND |  | CLOSED
VHLS851/852 | Cold Condensate outlet vent | HRSG lower NE |  |  | CND |  | CLOSED
VHLS829/830 | Cold condensate drain | HRSG lower NE |  |  | CND |  | CLOSED
VHLS801/802 | Drain after Heat Exchanger | HRSG lower NE |  |  | CND |  | CLOSED
VHLS807/810 | Drain after Heat Exchanger | HRSG lower NE |  |  | CND |  | CLOSED
VHLS821/823/824 | LP Economizer Drains (Block) | HRSG lower NW |  |  | CND |  | CLOSED
VHLS 913/916/918/920 | LP Economizer Drains (Root) | HRSG lower NW |  |  | CND |  | CLOSED
VCND352 | To ECA isolation | HRSG SE | ECA |  | CND |  | OPEN
VCND349 | Drain before FCV | HRSG SE | ECA |  | CND |  | OPEN
VCND410 | Vent after FCV | HRSG SE | ECA |  | CND |  | OPEN
VCND311 | ECA pump “A” suction valve | HRSG SE | ECA |  | CND |  | OPEN
VCND313 | ECA pump “B” suction valve | HRSG SE | ECA |  | CND |  | OPEN
VCND359 | ECA pump “A” discharge valve | HRSG SE | ECA |  | CND |  | OPEN
VCND314 | ECA pump “B” discharge valve | HRSG SE | ECA |  | CND |  | OPEN
VCND357/342 | ECA pump “A” DP | HRSG SE | ECA |  | CND |  | OPEN
| ECA pump “A” drain | HRSG SE | ECA |  | CND |  | CLOSED
| ECA pump “B” drain | HRSG SE | ECA |  | CND |  | CLOSED
VCND312/315 | ECA pump “B” DP | HRSG SE | ECA |  | CND |  | OPEN
VCND411 | ECA pump discharge vent | HRSG SE | ECA |  | CND |  | CLOSED
VCND335 | Pressure transmitter | HRSG SE | ECA |  | CND |  | OPEN
VCND197 | 2C cooler drain | HRSG SE | ECA |  | CND |  | CLOSED
VCND210 | 2C cooler vent | HRSG SE | ECA |  | CND |  | CLOSED
VCND240 | ECA cooler pressure transmitter | HRSG SE | ECA |  | CND |  | OPEN
VCND341 | ECA cooler drain | HRSG SE | ECA |  | CND |  | CLOSED
VCND407 | ECA cooler vent | HRSG SE | ECA |  | CND |  | CLOSED
VCND344 | ECA cooler pressure transmitter | HRSG SE | ECA |  | CND |  | OPEN
VCND408 | ECA drain | HRSG SE | ECA |  | CND |  | CLOSED
VCND243 | Isolation to 3-way valve | HRSG SE | ECA |  | CND |  | OPEN
VCND343 | To condensate system isolation | HRSG SE | ECA |  | CND |  | OPEN
VCND348 | Drain after FCV | HRSG SE | ECA |  | CND |  | CLOSED
VCND340 | Isolation after FCV | HRSG SE | ECA |  | CND |  | OPEN
VHBD 9806/9805 | LT iso | HRSG NE | BDT |  | HBD
VHBD 9902/9903 | LG drain | HRSG NE | BDT |  | HBD
VHBD 9804/9805 | LG iso | HRSG NE | BDT |  | HBD
VHBD 9802 | PIT | HRSG NE | BDT |  | HBD
VHBD 9904/9905 | BDT Quenching CV iso | HRSG NE | BDT |  | HBD
VHBD 9906 | BDT Quenching CV bypass | HRSG NE | BDT |  | HBD
VHBD 9907/9908 | BDT Quenching line drain | HRSG NE | BDT |  | HBD
VHBD 9901 | BD tank drain | HRSG NE | BDT |  | HBD
VSWS 100 | BD tank sump pump flush water | HRSG NE | BDT |  | HBD
VSWS 124 | BD tank sump A pump discharge | HRSG NE | BDT |  | HBD
VSWS 123 | BD tank sump B pump discharge | HRSG NE | BDT |  | HBD
VSWS 112 | BD tank sump pump discharge vent | HRSG NE | BDT |  | HBD
VBND 100/101 | BD tank sump pump discharge FT | HRSG NE | BDT |  | HBD
VSWS 101/102 | SW to BDT flow meter | HRSG NE | BDT |  | HBD
VSWS 111 | SW to BDT quenching iso | HRSG NE | BDT |  | HBD
VSWS 108 | SW to BDT quenching drain | HRSG NE | BDT |  | HBD
VSWS 109 | SW to HRSG sump pit quenching iso | HRSG NE | BDT |  | HBD
VSWS 110 | SW to HRSG sump pit quenching drain | HRSG NE | BDT |  | HBD
| HP/IP/LP intermittent blowdown drains | HRSG NE | BDT |  | HBD
VBDN687 | HRSGs sump discharge to WW sump | HRSG NE | BDT |  | HBD
VBDN 688/689 | HRSGs sump discharge to WW sump vent/drain | HRSG NE | BDT |  | HBD
VBDN 613 | HRSGs sump discharge to SW tank | HRSG NE | BDT |  | HBD
VBDN 614/615 | HRSGs sump discharge to SW tank vent/drain | HRSG NE | BDT |  | HBD
| IP continuous BD manual regulator (BD tank) | HRSG NE | BDT |  | HBD
| LP/IP/HP intermitent BD drains (in the pit) | HRSG NE | BDT |  | HBD
01-VAXS 133 | Steam to IP Evap vent | HRSG lower | HRSG |  | AXS
01-VHIS 909 | Steam to IP Evap MOV bypass | HRSG lower | HRSG |  | AXS
01-VHIS 860/861 | Steam to IP Evap drain after MOV | HRSG lower | HRSG |  | AXS
VHS 982/983 | IP superheater outlet sampl | HRSG lower | Sample
VBFW 211/212 | FW to HP interstage atemperator drain | HRSG West Landing | Attemperator HP |  |  |  | CLOSED
VHHS-830/831/832/833/834/835/836/837 | FW to HP interstage atemperator (2) flow transmitters | HRSG West Landing | Attemperator HP |  |  |  | OPEN
VHHS-863/864 | FW to HP interstage atemperator drain (2) valves | HRSG West Landing | Attemperator HP |  |  |  | CLOSED
VHHS-838/839/840/841 | FW to HP interstage atemperator strainer DP | HRSG West Landing | Attemperator HP |  |  |  | OPEN
VHHS-842/843 | FW to HP interstage atemperator strainer drain valve | HRSG West Landing | Attemperator HP |  |  |  | CLOSED
VHHS-844 | FW to HP interstage atemperator iso | HRSG West Landing | Attemperator HP |  |  |  | OPEN
VHHS-865/866 | FW to HP interstage atemperator vent | HRSG West Landing | Attemperator HP |  |  |  | CLOSED
VBFW265 | BFP "A" suction iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW 394F/159F/160F | BFP "A" suction PIT iso (3) (at the pump) | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW 404/405 | BFP "A" HP discharge PIT iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW406/407 | BFP "A" IP discharge PIT iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW 430/506 | BFP "A" IP FW discharge vent (2) valve | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFW269 | BFP "A" IP FW discharge iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
| BFP "A" IP FW discharge iso bypass | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
| BFP "A" IP FW discharge iso equalizing valve | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW 168/169 | BFP "A" IP FW discharge drain | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFV | BFP "A" IP FW discharge MOV equalizing valve | Pipe Rack 1st | BFP A |  | BFW
|  | Pipe Rack 1st | BFP A |  | BFW
VBFW 181/182/183/184/185/186/187/188 | BFP "A" HP FW flow meter iso (8) valves | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFV 189/190 | BFP "A" HP FW discharge vent (2) valves | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFV 192/193 | BFP "A" HP FW discharge drain (2) valves | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFV 271 | BFP "A" HP FW discharge iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFV 271 | BFP "A" HP FW discharge iso equalizing valve | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFV 271 | BFP "A" HP FW discharge iso bypass | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
V B F W 604/605 | BFP "A" HP FW discharge vent (2) valves | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFW 194/195 | BFP "A" HP FW discharge drain (2) valves | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
| BFP "A" HP FW discharge MOV equalizing valve | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW147/150 | BFP "A" HP FW recirc vent (second pipe rack) | Pipe Rack 2nd | BFP A |  | BFW |  | CLOSED
VBFW 138/139 | BFP "A" HP FW recirc drain (under first pipe rack) | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VHLS 924 | BFP suction iso | one level down under LP drum | BFP A/B suction |  | BFW |  | OPEN
VBFW 149 | BFP suction header drain | Pipe Rack 1st | BFP A/B suction |  | BFW |  | CLOSED
VBFW152 | BFP suction iso | Pipe Rack 1st | BFP A/B suction |  | BFW |  | OPEN
VBFW132 | BFP suction PIT iso | Pipe Rack 1st | BFP A/B suction |  | BFW |  | OPEN
VBFW154/155 | BFP suction strainer DPT | Pipe Rack 1st | BFP A/B suction |  | BFW |  | OPEN
VBFW | BFP suction strainer blowdown | Pipe Rack 1st | BFP A/B suction |  | BFW |  | CLOSED
VBFW 264 | BFP suction from condensate | Pipe Rack 1st | BFP A/B suction |  | BFW |  | OPEN
VBFW266 | BFP "B" suction iso | Pipe Rack 1st | BFP B |  | BFW |  | OPEN
VBFW 180F/179F/395F | BFP "B" suction PIT iso (3) | Pipe Rack 1st | BFP B |  | BFW |  | OPEN
VBFW 177/178 | BFP "B" HP discharge PIT iso | Pipe Rack 1st | BFP B |  | BFW |  | OPEN
VBFW 170/171 | BFP "B" IP discharge PIT iso | Pipe Rack 1st | BFP B |  | BFW IP |  | OPEN
VBFW 172/173 | BFP "B" IP FW discharge vent (2) valve | Pipe Rack 1st | BFP B |  | BFW IP |  | CLOSED
VBFW 270 | BFP "B" IP FW discharge iso | Pipe Rack 1st | BFP B |  | BFW IP |  | OPEN
VBFW | BFP "B" IP FW discharge iso bypass | Pipe Rack 1st | BFP B |  | BFW IP |  | CLOSED
VBFW | BFP "B" IP FW discharge iso equalizing valve | Pipe Rack 1st | BFP B |  | BFW IP |  | OPEN
VBFW 175/176 | BFP "B" IP FW discharge drain | Pipe Rack 1st | BFP B |  | BFW IP |  | CLOSED
| BFP "B" IP FW discharge MOV equalizing valve | Pipe Rack 1st | BFP B |  | BFW IP |  | OPEN
VBFW 219/220/221/222/223/224/225/226 | BFP "B" HP FW flow meter iso (8) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | OPEN
VBFW 227/228 | BFP "B" HP FW discharge vent (2) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 235/236 | BFP "B" HP FW discharge drain (2) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 272 | BFP "B" HP FW discharge iso | Pipe Rack 1st | BFP B |  | BFW HP |  | OPEN
VBFW | BFP "B" HP FW discharge iso equalizing valve | Pipe Rack 1st | BFP B |  | BFW HP |  | OPEN
VBFW | BFP "B" HP FW discharge iso bypass | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 606/607 | BFP "B" HP FW discharge vent (2) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 237/238 | BFP "B" HP FW discharge drain (2) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW | BFP "B" HP FW discharge MOV equalizing valve | Pipe Rack 1st | BFP B |  | BFW HP |  | OPEN
VBFW 209/210 | BFP "B" HP FW recirc vent (second pipe rack) | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 267/337 | BFP "B" HP FW recirc drain (under first pipe rack) | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 416/417 | IP FW header Vent | Pipe Rack 1st | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 918 | IP economizer Vent | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 915/917 | IP Economizer Vents (Root) | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 922/923 | FW to IP drum PIT (2) iso valves | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 924/925/926/927/928/929/930/931 | FW to IP drum FT (8) iso valves, 2 transmitters | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 934 | FW to IP drum before CV isolation | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 934 | FW to IP drum before CV isolation bypass | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 934 | FW to IP drum before CV isolation equalizing | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 936 | FW to IP drum CV bypass | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 935 | FW to IP drum after CV isolation | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 935 | FW to IP drum after CV isolation bypass | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 935 | FW to IP drum after CV isolation equalizing | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 933/932 | Drain before CV | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 854/855 | Drain before CV Iso valve | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 937/938 | Drain after CV | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 992 | Phosphate injection iso | HRSG upper West | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 950/951/952/953 | Level Transmitter | HRSG upper West | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 939/940/993/979 | Level Element | HRSG upper West | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS | Level Gauge (2) valves | HRSG upper West | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 941/942/944 | Level instrumnt blowdown | HRSG upper West | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 954/955/956/957/958/959/960/961 | Level Transmitter (8) iso valves, 2 transmitters | HRSG upper East | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 943/948/947/949 | Level Element | HRSG upper East | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS | Level Gauge | HRSG upper East | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 945/946 | Level instrumnt blowdown | HRSG upper East | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 846/847/849/850/851/976/977 | 4 vents to atmosphere (8) iso valves | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 963/964/965/966 | IP drum (2) PIT (4) iso valves | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 971 | Nitrogen Fill iso | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 967/968/969/970 | Nitrogen (2) PIT (4) iso valves | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 998/999 | Pegging steam to LP drum vent (2) iso valves | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 978 | Pegging steam to LP drum iso | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 978 | Pegging steam to LP drum iso bypass | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 978 | Pegging steam to LP drum iso equalizing | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 973/974 | IP drum water sample (2) valves | Under IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 852/853 | IP sparging steam strainer drain (2) valves (under HRSG) | HRSG lower West | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 860/861 | IP sparging steam drain (2) valves | HRSG lower West | HRSG/ IP Drum |  | HIS |  | CLOSED
VBFW 199 | HP BFW PIT to the HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VBFW 200 | HP BFW PIT to the HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VBFW 116 | Drain after HP cold fill iso | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VBFW 608 | HP BFW header to HRSG vent | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VBFW 609 | HP BFW header to HRSG vent | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VHHS 918F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 919F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 920F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 921F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 922F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 923F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 924F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 925F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VBFW 422 | HP BFW header drain (2) valves | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VBFW 423 | HP BFW header drain (2) valves | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VHHS 939/940/941/942/943/944/945/946 | HP economizer vent root valves | HRSG upper | HRSG/ HP Drum |  | BFW HP |  | CLOSED
VHHS 947 | HP economizer vent root valve | HRSG upper | HRSG/ HP Drum |  | BFW HP |  | OPEN
VHHS 988 | Phosphate injection iso | HRSG upper West | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 967/968/969/970 | Level Transmitter (4) valves | HRSG upper West | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 963/964/986/987 | Level Element (4) valves | HRSG upper West | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS | Level Gauge (2) valves | HRSG upper West | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 965/966/972 | Level instruments blowdown | HRSG upper West | HRSG/ HP Drum |  | HHS |  | CLOSED
VHHS 991/992 | HP drum water sample (2) valves | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 904 | HP continuous blowdown iso | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS | HP continuous blowdown regulator | HRSG upper East | HRSG/ HP Drum |  | HHS
VHHS 975/976/977/978/979/980/981/982 | (2)Level Transmitters (8) valves | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 971/983/984/985 | Level Element (4) valves | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS | Level Gauge (2) valves | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 973/974 | Level instruments blowdown | HRSG upper East | HRSG/ HP Drum |  | HHS |  | CLOSED
VHHS 959 | Nitrogen Fill iso | Top of the HP drum | HRSG/ HP Drum |  | HHS |  | CLOSED
VHHS 956/957 | Nitrogen PIT (2) valves | Top of the HP drum | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 950/951/952/953 | (2) HP Drum PIT (4) valves | Top of the HP drum | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 801/802 | HP drum vent (2) valves | Top of the HP drum | HRSG/ HP Drum |  | HHS |  | CLOSED
VHHS 998/999 | HP saturated steam sample (2) valves (under HP drum) | Top of the HP drum |  |  | HHS |  | OPEN
VHHS 996/997 | HP sparging steam strainer drain (2) valves (under HRSG) | Top of the HP drum |  |  | HHS |  | CLOSED
VBFW 375/521 | FW to HP terminal atemperator strainer #1 inlet | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 523/555 | FW to HP terminal atemperator strainer #1 outlet | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 246/247 | FW to HP terminal atemperator strainer #1 vent | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 380/509 | FW to HP terminal atemperator strainer #1 drain | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 549/376 | FW to HP terminal atemperator strainer #2 inet | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 383/525 | FW to HP terminal atemperator strainer #2 outlet | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 248/249 | FW to HP terminal atemperator strainer #2 vent | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 503/377 | FW to HP terminal atemperator strainer #2 drain | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 242/243/244/245 | FW to HP terminal atemperator strainer PDIT | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 385F/507F/533F/515F/117F/120F/121F/122F | FW to HP terminal atemperator (3) Flow meters | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 563/565 | FW to HP terminal atemperator vent after flow meters | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 545/547 | FW to HP terminal atemperator drain after block valve | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 531/505 | FW to HP terminal atemperator iso after CV | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 529/553 | FW to HP terminal atemperator drain | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 240/241 | FW to HP terminal atemperator drain after check valve | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 438/424 | IP FW header PIT | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | OPEN
VBFW 106/111 | IP FW strainer #1 inlet iso | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | OPEN
VBFW 107/108 | IP FW strainer #1 outlet iso | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | OPEN
VBFW 101/115 | IP FW strainer #1 drain | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 151/161 | IP FW strainer #1 vent | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 388/105 | IP FW strainer #2 inlet iso | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 391/109 | IP FW strainer #2 outlet iso | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 113/390 | IP FW strainer #2 drain | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 162/163 | IP FW strainer #2 vent | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 128/129 | HP steam bypass spray CV iso | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | OPEN
VBFW 130/131 | HP steam bypass spray drain | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 124/125/112/378/114/519/126/127 | IP FW to HP bypass FT iso | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | OPEN
VBFW 569/567 | IP FW to HP bypass vent | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 119/387 | IP FW to HP bypass drain before CV | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 513 | IP FW to HP bypass iso | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 557/551 | IP FW to HP bypass drain | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 574/575 | HRH terminal attemperator before CV iso | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 576/577 | HRH terminal attemperator drain | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 124F/125F/126F/127F/100F/110F/104F/102F | HRH terminal atemperator flow meter (3 tramsmitters) | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 389/103 | HRH terminal drain after block valve (2) valves | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 118 | HRH terminal attemperator after CV iso | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 362/363 | HRH terminal drain after check valve (2) valves (3rd pipe rack) | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 618/619 | HRH terminal attemperator vent after check (3rd pipe rack) | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 918/919/820/821/822/823/824/825 | (2) Flow transmitters (8) valves | HRSG lower | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 960/961 | Drain before CV | HRSG lower | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 848/849 | Strainer Drain (2) valves | HRSG lower | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 826/827/828/829 | Strainer DPT (4) valves | HRSG lower | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 930 | After CV iso | HRSG lower | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 962/963 | Drain after check (2) valves | HRSG lower | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW433/434 | CRH to AUX steam LOW flow attemperator ISO before CV | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW447/448 | Drain between attemperator isolation valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 431/432/156/157 | Flow transmitter (4) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 436/437 | Drain before CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 624/625 | Vent after CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 628/629 | Drain after CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 319 | CRH to AUX steam LOW flow attemperator ISO after CV | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 451/452 | Drain after check (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 570/571 | CRH to AUX steam HIGH flow attemperator ISO before CV | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 572/573 | Drain between attemperator isolation valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 140/141/142/143 | Flow transmitter (4) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 144/145 | Drain before CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 622/623 | Vent after CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 626/627 | Drain after CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 146 | CRH to AUX steam HIGH flow attemperator ISO after CV | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 454/453 | Drain after check (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 113/390 | IP FW strainer #2 drain | Pipe Rack 1st | TCA |  | BFW IP |  | CLOSED
VBFW 162/163 | IP FW strainer #2 vent | Pipe Rack 1st | TCA |  | BFW IP |  | CLOSED
VBFW 296/297/298/299 | FW to TCA flow meter (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 300 | FW to TCA iso | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 301/302 | FW to TCA drain | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VBFW 303/304 | FW to TCA drain after CV | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VBFW 306 | From TCA iso | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 700/701/929/928 | PDI across TCA | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 307/308/309/310 | FW from TCA PITx2 (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 305/294 | Drain After TCA coller | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VBFW 311/312/313/314 | From TCA flow meter (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 315/316/317/318 | From TCA flow meter (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 324/325 | From TCA to HP economizer vent | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VBFW 320/321/326/327 | From TCA to HP economizer PDIT (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 328/329 | From TCA to HP economizer drain after CV | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VHHS 948 | From TCA to HP economizer isolation | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VHHS 949 | From TCA to HP economizer isolation bypass | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VHHS 950 | From TCA to HP economizer isolation equalizing | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 331/332 | From TCA to Cond. Receiver Tank vent | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 610/611 | From TCA to Cond. Receiver Tank drain | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 614/615 | From TCA to Cond. Receiver Tank vent (smr bldng) | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 330/922 | From TCA to Cond. Receiver Tank iso (2) vlvs | CRT | TCA |  | BFW HP |  | OPEN
VBFW 165/166 | From TCA to Cond. Receiver Tank drain | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 923/532 | From TCA to Cond. Receiver Tank strainer vent | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 333/334 | From TCA to Cond. Receiver Tank strainer drain | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 322/323 | From TCA to Cond. Receiver Tank vent after srtainer | CRT | TCA |  | BFW HP |  | CLOSED
VBFW305/306 | From TCA to Cond. Receiver Tank drain after strainer | CRT | TCA |  | BFW HP |  | OPEN
VBFW | From TCA to Cond. Receiver Tank before CV iso | CRT | TCA |  | BFW HP |  | OPEN
VBFW339 | From TCA to Cond. Receiver Tank after CV iso | CRT | TCA |  | BFW HP |  | OPEN
VBFW | To Gas performance heater MOV bypass | one level under LP Drum | FGPH |  | BFW IP |  | CLOSED
VBFW461/462 | Drain berore startap heater | Pipe Rack 1st | FGPH |  | BFW IP |  | CLOSED
VBFW 120/121 | Startup heater drain | Pipe Rack 1st | FGPH |  | BFW IP |  | CLOSED
VBFW 117/110 | Startup heater vent | Pipe Rack 1st | FGPH |  | BFW IP |  | CLOSED
VBFW 578/579 | Vent after startap heater | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 340/341/342/343 | Gas performance heater flow | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 344 | Gas performance heater High flow CV iso (before) | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW345 | Gas performance heater High flow CV iso (after) | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW3346 | Gas performance heater Low flow CV iso (before) | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 347 | Gas performance heater Low flow CV iso (after) | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 285/348 | Gas performance heater nitrogen connection (after CV) | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 350/352 | Gas performance heater iso | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 351/286 | Gas performance heater drain | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 284/262 | Gas performance heater FW in PIT | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW357/274/356/273 | Gas performance heater Level switch vessel 1 | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW354/355/275/276 | Gas performance heater Level switch vessel 1 | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 153/353 | Gas performance heater Level switch vessel 1 vent | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 372/373/2278/279 | Gas performance heater Level switch vessel 2 | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 370/371/280/281 | Gas performance heater Level switch vessel 2 | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW369/277 | Gas performance heater Level switch vessel 2 vent | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 359/282 | Gas performance heater FW out PIT | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 602/603 | Drain after Gas performance heater | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 616/617 | Gas performance heater drain | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 349/283 | Gas performance heater vent | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 289/360 | Gas performance heater drain before block valve | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW291/364 | Gas performance heater drain before CV | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 367 | Gas performance heater outlet iso | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW600/601 | Gas performance heater to receiver tank vent | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 290/361 | Gas performance heater to receiver tank iso (2) valves | CRT | FGPH |  | BFW IP |  | OPEN
VBFW 402/403 | Gas performance heater to receiver tank drain | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 440/441 | Gas performance heater to receiver tank strainer vent | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 292/366 | Gas performance heater to receiver tank strainer drain | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW449/450 | Gas performance heater to receiver tank after strainer drain | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 459/460 | Gas performance heater to receiver tank after strainer vent | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 379 | Gas performance heater to receiver tank iso after CV | CRT | FGPH |  | BFW IP |  | OPEN
VHLS 819/820/821/822/825/826/827/828 | LP steam flow transmitters | Pipe Rack 2nd | HRSG |  | HLS
VLPS 112/123 | LP steam header vents | Pipe Rack 2nd | HRSG |  | HLS
VHHS 818/819 | HP superheater outlet vent to atmoshpere (before MOV) | HRSG upper | HRSG |  | HHS
VHHS 998/999 | HP saturated steam sample (under HP drum) | HRSG upper | HRSG |  | HHS
VHHS 813/814/871/872/873/874 | HP superheater outlet PITs (before MOV) | HRSG upper | HRSG |  | HHS
VHHS 906 | 906 MOV bypass (HP steam isolation) | HRSG upper | HRSG/ST |  | HHS
VHHS 907 | 907 MOV bypass (HP steam isolation) | HRSG upper | HRSG/ST |  | HHS
VHPS 111/112 | HPS header vent | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 113/114/115/116 | HPS header PITs | Pipe Rack 3rd | HRSG/ST |  | HHS
VHHS 820/821/822/823/824/825/826/827 | HP steam FT before terminal attemperator | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 123/124/125/126/127/130 | HP steam FT after terminal attemperator | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 137/138 | HPS Bypass warmup line vent | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 828F/829F | HPS superheated steam sample isolation | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 128/129 | HPS Bypass vent | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 119/120/121/122 | HPS Bypass PITs | Pipe Rack 3rd | HRSG/ST |  | HHS
VCRH 186/115 | CRH header vent | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 159/165 | CRH header vent | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 148/166 | CRH header PT | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 169/170/171/172/117/122/137/146 | CRH header Drip Leg Level Switches | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 174/124/147/173 | CRH header Drip Leg Level Switche drains | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH119/167/118/168 | CRH header Drip Leg Level Switche vents | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 111 | CRH header Drip Leg AOV iso | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 136/185 | CRH header Drip Leg drain | Pipe Rack 2nd | HRSG/ST |  | CRH
VHRS 803/804 | CRH header PIT (HRSG) | HRSG upper | HRSG/ST |  | HRH
VHRS 909 | Nitrogen to CRH | HRSG upper | HRSG/ST |  | HRH
VHRS 807/808 | Nitrogen to CRH vent | HRSG upper | HRSG/ST |  | HRH
VHRS 969/970 | Reheater interstage Dripleg drain | HRSG upper | HRSG/ST |  | HRH
VHRS 903/904/911/912/813/814 | Reheater outet PITs | HRSG upper | HRSG/ST |  | HRH
VHRH 101/107 | HRH header vent | Pipe Rack 3rd | HRSG/ST |  | HRH
VHRH 135/136/187/188 | HRH header PIT (before attemperator) | Pipe Rack 3rd | HRSG/ST |  | HRH
VHRS 901/902 | HRH sample | Pipe Rack 3rd | HRSG/ST |  | HRH
VHRH 100/102/103/104/121/106 | HRH header PIT (after attemperator) | Pipe Rack 3rd | HRSG/ST |  | HRH
VHRH 108/109 | HRH header vent | Pipe Rack 3rd | HRSG/ST |  | HRH
VSTP 123 | GSC drain trap bypass | ST lower | ST seals |  | STP
VSTP 137 | GSC drain trap vent | ST lower | ST seals |  | STP |  | OPEN
VSTP 122 | GSC drain trap strainer drain | ST lower | ST seals |  | STP
VSTP 146/147/153/154 | GS Exhauster drains | ST lower | ST seals |  | STP
MAW01AA001 | GS Exhauster A inlet | ST upper West | ST seals |  | STP
MAW01AA002 | GS Exhauster B inlet | ST upper West | ST seals |  | STP
VSTP 125 | GS Exhauster A outlet | ST upper West | ST seals |  | STP
VSTP 179 | GS Exhauster B outlet | ST upper West | ST seals |  | STP
VAX 159 | GS supply iso before superheater | ST lower | ST seals |  | STP
VAXS 101 | GS supply vent before superheater | ST lower | ST seals |  | STP
VAXS 104/105 | GS superheater drain trap | ST lower | ST seals |  | STP
VAXS 107 | GS superheater drain trap bypass | ST lower | ST seals |  | STP
VAXS 106 | GS superheater drain trap strainer drain | ST lower | ST seals |  | STP
VAXS 196/197/198 | GS supply drain valves | ST lower | ST seals |  | STP
VSTP 148/149 | GS supply CV isolations | ST upper West | ST seals |  | STP
VSTP204 | GS supply CV bypass | ST upper West | ST seals |  | STP
VSTP 159/181 | GS mist separator orphis drain | ST lower | ST seals |  | STP
VSTP 167 | GS mist separator orphis bypass | ST lower | ST seals |  | STP
VSTP 182 | GS mist separator common drain | ST lower | ST seals |  | STP
VSTP 131/133 | GS header PT | ST lower | ST seals |  | STP
VSTP 183/184/185 | GS header drain | ST lower | ST seals |  | STP
VSTP 127/129 | GS spill over CV iso | ST lower | ST seals |  | STP
VSTP 132 | GS spill over CV bypass | ST lower | ST seals |  | STP
01-VAXS 171 | Steam to startup heater iso | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 109/110 | Startup Heater LIT isolation valves | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 121 | Steam to Startup Heater vent | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 124/125 | Drain from Startup Heater FC isolation valves | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 126 | Drain from Startup Heater line drain | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 127/156 | Drain from Startup Heater FC bypass | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VSMP 130F | Aux steam sample iso | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 187/188 | Aux steam header PITs | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 132 | Aux steam header vent (stmr bldg) | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS |  | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 200 | Drain before steam trap | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 117/201 | Steam trap iso | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 120 | Steam Trap bypass | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 119 | Steam Trap strainer drain | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 190 | Drain before steam trap | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 191/194 | Steam trap iso | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 202 | Steam Trap bypass | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 195 | Steam Trap strainer drain | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VCRH 180/183 | CRH to Aux steam FC iso (Low flow) | Pipe Rack 3rd | Aux Steam Header |  | CRH
01-VCRH 181/184 | CRH to Aux steam FC iso (High flow) | Pipe Rack 3rd | Aux Steam Header |  | CRH
01-VCRH 120/162 | CRH to Aux steam vent | Pipe Rack 3rd | Aux Steam Header |  | CRH
01-VCRH 121/182 | CRH to Aux steam vent | Pipe Rack 3rd | Aux Steam Header |  | CRH
02-VAXS 189/290 | Steam to HP Evap Steam trap ISOs |  | Sparging
02-VAXS 289 | Steam to HP Evap Steam trap bypass |  | Sparging
02-VAXS 144 | Steam to HP Evap Steam trap strainer drain |  | Sparging
02-VAXS 291 | Steam to HP Evap drain before steam trap |  | Sparging
VHHS 904 | Steam to HP Evap MOV bypass |  | Sparging
VHHS 994/995 | Steam to HP Evap drain after MOV |  | Sparging
VHHS 996/997 | Steam to HP Evap strainer drain |  | Sparging
02-VAXS 133 | Steam to IP Evap vent | HRSG lower | Sparging |  | AXS
02-VHIS 909 | Steam to IP Evap MOV bypass | HRSG lower | Sparging |  | AXS
02-VHIS 860/861 | Steam to IP Evap drain after MOV | HRSG lower | Sparging |  | AXS
02-VHIS 852/853 | Steam to IP Evap strainer drain | HRSG lower | Sparging |  | AXS
02-VHLS 904 | Steam to LP Evap MOV bypass | HRSG lower | Sparging |  | AXS
02-VHLS 985/999 | Steam to LP Evap drain after MOV | HRSG lower | Sparging |  | AXS
02-VHLS 992/993 | Steam to LP Evap strainer drain | HRSG lower | Sparging |  | AXS
02-VAXS 135/136 | Steam to LP Evap Steam trap iso | HRSG lower | Sparging |  | AXS
02-VAXS 138 | Steam to LP Evap Steam trap bypass | HRSG lower | Sparging |  | AXS
02-VAXS 137 | Steam to LP Evap Steam trap strainer drain | HRSG lower | Sparging |  | AXS
02-VAXS 113 | Steam to LP Evap Drain before Steam trap | HRSG lower | Sparging |  | AXS
02-VAXS 155 | Drain before steam trap | HRSG lower West |  |  | AXS
02-VAXS 112/115 | Steam trap iso | HRSG lower West |  |  | AXS
02-VAXS 129 | Steam Trap bypass | HRSG lower West |  |  | AXS
02-VAXS 116 | Steam Trap strainer drain | HRSG lower West |  |  | AXS
02-VAXS 130 | Drain before steam trap | HRSG lower West |  |  | AXS
02-VAXS 103/161 | Steam trap iso | HRSG lower West |  |  | AXS
02-VAXS 164 | Steam Trap bypass | HRSG lower West |  |  | AXS
02-VAXS 160 | Steam Trap strainer drain | HRSG lower West |  |  | AXS
02-VAXS 292 | Aux steam header vent | HRSG lower West |  |  | AXS
00-VFGS220 | Emergency Shut Off Valve inlet isolation | GAS YARD | GAS YARD |  | FGS |  | Open
00-VFGS230 | Emergency Shut Off Valve inlet isolation | GAS YARD | GAS YARD |  | FGS |  | Open
00-VFGS221 | N2 Purge Isolation (fenced gas yard) | GAS YARD | GAS YARD |  | FGS |  | Closed
00-VFGS222 | N2 Purge Isolation (fenced gas yard) | GAS YARD | GAS YARD |  | FGS |  | Closed
00-VFGS803 | FILTER/SEPERATOR NITROGEN PURGE/VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS703 | FILTER/SEPERATOR NITROGEN PURGE/VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS719 | FILTER/SEPERATOR LEVEL CONTROL VALVE INLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS720 | FILTER/SEPERATOR LEVEL CONTROL VALVE OUTLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS722 | FILTER/SEPERATOR LEVEL CONTROL BYPASS |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS723 | FILTER/SEPERATOR LEVEL CONTROL VALVE INLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS724 | FILTER/SEPERATOR LEVEL CONTROL VALVE OUTLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS726 | FILTER/SEPERATOR LEVEL CONTROL BYPASS |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS819 | FILTER/SEPERATOR LEVEL CONTROL VALVE INLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS820 | FILTER/SEPERATOR LEVEL CONTROL VALVE OUTLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS822 | FILTER/SEPERATOR LEVEL CONTROL BYPASS |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS823 | FILTER/SEPERATOR LEVEL CONTROL VALVE INLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS824 | FILTER/SEPERATOR LEVEL CONTROL VALVE OUTLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS826 | FILTER/SEPERATOR LEVEL CONTROL BYPASS |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS705 | FILTER/SEPERATOR NITROGEN PURGE/VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS805 | FILTER/SEPERATOR NITROGEN PURGE/VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS708 | FILTER/SEPERATOR LEVEL COLUM SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS707 | FILTER/SEPERATOR LEVEL COLUM SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS711 | FILTER/SEPERATOR LEVEL GAGE SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS712 | FILTER/SEPERATOR LEVEL GAGE SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS708V | FILTER/SEPERATOR LEVEL GAGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS708D | FILTER/SEPERATOR LEVEL GAGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS704D | FILTER SEPERATOR COLUM DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS718 | FILTER/SEPERATOR LEVEL COLUM SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS717 | FILTER/SEPERATOR LEVEL COLUM SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS713 | FILTER/SEPERATOR LEVEL GAGE SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS714 | FILTER/SEPERATOR LEVEL GAGE SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS718V | FILTER/SEPERATOR LEVEL GAGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS718D | FILTER/SEPERATOR LEVEL GAGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS714D | FILTER SEPERATOR COLUM DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS709 | FILTER SEPERATOR LEVEL SWITCH ISOLATION LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS710 | FILTER SEPERATOR LEVEL SWITCH ISOLATION UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS715 | FILTER SEPERATOR LEVEL SWITCH ISOLATION LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS716 | FILTER SEPERATOR LEVEL SWITCH ISOLATION UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS704 | FILTER SEPERATOR DP TRANSMITTER HIGH SIDE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS706 | FILTER SEPERATOR DP TRANSMITTER LOW SIDE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS808 | FILTER/SEPERATOR LEVEL COLUM SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS807 | FILTER/SEPERATOR LEVEL COLUM SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS811 | FILTER/SEPERATOR LEVEL GAGE SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS812 | FILTER/SEPERATOR LEVEL GAGE SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS808V | FILTER/SEPERATOR LEVEL GAGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS808D | FILTER/SEPERATOR LEVEL GAGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS804D | FILTER SEPERATOR COLUM DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS818 | FILTER/SEPERATOR LEVEL COLUM SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS817 | FILTER/SEPERATOR LEVEL COLUM SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS813 | FILTER/SEPERATOR LEVEL GAGE SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS814 | FILTER/SEPERATOR LEVEL GAGE SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS818V | FILTER/SEPERATOR LEVEL GAGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS818D | FILTER/SEPERATOR LEVEL GAGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS814D | FILTER SEPERATOR COLUM DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS809 | FILTER SEPERATOR LEVEL SWITCH ISOLATION LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS810 | FILTER SEPERATOR LEVEL SWITCH ISOLATION UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS815 | FILTER SEPERATOR LEVEL SWITCH ISOLATION LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS816 | FILTER SEPERATOR LEVEL SWITCH ISOLATION UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS804 | FILTER SEPERATOR DP TRANSMITTER HIGH SIDE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS806 | FILTER SEPERATOR DP TRANSMITTER LOW SIDE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS731 | FILTER SEPERATOR DRAIN TANK DRAIN VALVE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS727 | FILTER SEPERATOR DRAIN TANK LEVEL IND. TRANSMITTER LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS728 | FILTER SEPERATOR DRAIN TANK LEVEL IND. TRANSMITTER UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS736 | FILTER SEPERATOR DRAIN TANK LEVEL TRASMITTER DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS729 | FILTER SEPERATOR DRAIN TANK LEVEL GAUGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS730 | FILTER SEPERATOR DRAIN TANK LEVEL GAUGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS732 | FILTER SEPERATOR DRAIN TANK LEVEL SWITH LOWER ISO. |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS735 | FILTER SEPERATOR DRAIN TANK LEVEL SWITH UPPER ISO. |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS736 | FILTER SEPERATOR DRAIN TANK LEVEL SWITH DRAIN ISO. |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS733 | 12” FLOW METER STATION INLET |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS733D | 12” FLOW METER STATION INLET VALVE DRAIN |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS734 | 6” FLOW METER INLET |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS734D | 6” FLOW METER INLET VALVE DRAIN |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS744 | 6” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS748 | 6” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS747 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS743 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS737 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS739 | 12" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS741 | 12" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS745 | 12" YV-745 DRAIN VALVE |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS740 | 6" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS742 | 6" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS746 | 6" YV-746 DRAIN VALVE |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS833 | 12” FLOW METER STATION INLET |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS833D | 12” FLOW METER STATION INLET VALVE DRAIN |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS834 | 6” FLOW METER INLET |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS834D | 6” FLOW METER INLET VALVE DRAIN |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS844 | 6” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS848 | 6” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS847 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS843 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS837 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS839 | 12" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS841 | 12" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (04) |  | FGS |  | P[EN
00-VFGS845 | 12" YV-845 DRAIN VALVE |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS840 | 6" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS842 | 6" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS846 | 6" YV-846 DRAIN VALVE |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS 229 | GAS SUPPLY ISOLATION TO HEATER |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS
00-VFGS245 | glycol supply to glycol heater |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | Open
00-VFGS246 | Glycol recirc pump skid isolation from fuel gas heat exchanger |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | Open
00-VFGS981 | GLYCOL FILL ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS984 | GLYCOL TANK SEPERATOR DRAIN VALV |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS976 | GLYCOL EXPANSION TANK ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS977 | GLYCOL EXPANSION TANK VENT |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS987 | GLYCOL EXPANSION TANK DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS968 | GLYCOL PUMP SUCTION TRANSMITTER ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS969 | GLYCOL PUMP SUCTION TRANSMITTER ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS968A | GLYCOL PUMP "A" SUCTION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS969A | GLYCOL PUMP "A" SUCTION STRAINER DP ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS970A | GLYCOL PUMP "A" SUCTION STRAINER DP ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS971A | GLYCOL PUMP "A" SUCTION STRAINER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS974A | GLYCOL PUMP "A" DISCHARGE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS973A | GLYCOL PUMP "A" DISCHARGE DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS972A | RECIRC ISOLATION PUMP "A" |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS968B | GLYCOL PUMP "B" SUCTION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS969B | GLYCOL PUMP "B" SUCTION STRAINER DP ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS970B | GLYCOL PUMP "B" SUCTION STRAINER DP ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS971B | GLYCOL PUMP "B" SUCTION STRAINER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS974B | GLYCOL PUMP "B" DISCHARGE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS973B | GLYCOL PUMP "B" DISCHARGE DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS972B | RECIRC ISOLATION PUMP "B" |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS974 | GLYCOL PUMPS DISCHARGE PRESSURE TRANSMITTER |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS975 | GLYCOL PUMPS DISCHARGE PRESSURE TRANSMITTER |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS983 | GLYCOL HEATER DP GUAGE HIGH SIDE ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS951 | GLYCOL HEATER DP GUAGE LOW SIDE ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS953 | GLYCOL HEATER DP DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS984 | GLYCOL HEATER DP DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS985 | GLYCOL HEATER GAS ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS986 | GLYCOL HEATER GAS STRAINER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS001 | GLYCOL HEATER GAS FLOW METER INLET VALVE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS002 | GLYCOL HEATER GAS FLOW METER INLET DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS021 | GLYCOL HEATER GAS PILOT ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS025 | GLYCOL HEATER PILOT HEADER DRAIN VALVE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS027 | GLYCOL HEATER PILOT HEADER DRAIN VALVE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS028 | GLYCOL HEATER PILOT GAS TO BURNER ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS007 | GLYCOL HEATER MAIN GAS HEADER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS009 | GLYCOL HEATER MAIN GAS HEADER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS016 | GLYCOL HEATER MAIN GAS HEADER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS018 | GLYCOH HEATER MAIN GAS ISOLATION BEFORE BURNER |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS755 | GLYCOL HEAT EXCHANGER NITROGEN PURGE/VENT (GAS SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS758 | GLYCOL HEAT EXCHANGER NITROGEN PURGE/VENT (GAS SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS855 | GLYCOL HEAT EXCHANGER NITROGEN PURGE/VENT (GAS SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS858 | GLYCOL HEAT EXCHANGER NITROGEN PURGE/VENT (GAS SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS959 | GLYCOL HEATER VENT (GLYCOL SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS958 | GLYCOL HEATER DRAIN (GLYCOL SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS965 | GLYCOL HEATER VENT (GLYCOL SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS964 | GLYCOL HEATER DRAIN (GLYCOL SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS224 | glycol heat exchanger bypass/temperature control valve #1 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | THROTTLED
00-VFGS225 | glycol to fuel gas heat exchanger inlet #1 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | Open
00-VFGS226 | glycol from fuel gas heat exchanger outlet #1 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | Open
00-VFGS238 | glycol to fuel gas heat exchanger inlet #2 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS239 | glycol from fuel gas heat exchanger outlet #2 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS240 | glycol heat exchanger bypass/temperature control valve #2 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS152 | GLYCOL HEAT EXCHANGER VENT |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS151 | GLYCOL HEAT EXCHANGER VENT |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS246 | GLYCOL RECIRC PUMP INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS245 | GLYCOL RECIRC PUMP OUTLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS150 | GLYCOL SUPPLY VENT/DRAIN |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS853 | PRESS TRANSMITTER ISOLATION #2 HEAT EXCHANGER INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS859 | PRESS TRANSMITTER ISOLATION #2 HEAT EXCHANGER INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS753 | PRESS TRANSMITTER ISOLATION #1 HEAT EXCHANGER INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS759 | PRESS TRANSMITTER ISOLATION #1 HEAT EXCHANGER INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS200 | SKID08 HP reg station outlet to CT FUEAL GAS HEADER |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS782 | 6” OUTLET TO ELECTRIC HEATER NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS783 | 6” OUTLET TO ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS776 | 8” LOW FLOW REGULATING STATION INLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS776D | 8” LOW FLOW REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS782 | LOW FLOW NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS790 | LOW FLOW REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS793 | LOW FLOW REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS777 | 8” LOW FLOW REGULATING STATION INLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS777D | 8” LOW FLOW REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS794 | REDUCED GAS HEADER NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | Closed
00-VFGS774 | 16” SEC. REGULATING STATION INLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS774D | 16” SEC. REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS781 | SEC. REG. STATION NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS789 | SEC. REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS792 | SEC. REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS775 | 16” SEC. REGULATING STATION OUTLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS775D | 16” SEC. REGULATING STATION OUTLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS772 | 16” PRI. REGULATING STATION INLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS772D | 16” PRI. REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS780 | PRI. REG. STATION NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | Closed
00-VFGS788 | PRI. REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS791 | PRI. REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS773 | 16” PRI. REGULATING STATION OULET |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS773D | 16” PRI. REGULATING STATION OULET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS783 | 6” OUTLET TO ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS253 | SKID08 HP reg. station outlet to fuel gas compressors |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS258 | N2 Purge Isolation |  | HP REGULATING STATION (08) |  | FGS |  | Closed
00-VFGS261 | GAS TO LP HEATER VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS262 | GAS TO LP HEATER VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS263 | COMMON ISOLTION AFTER ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS260 | COMMON ISOLTION BEFORE ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS259/783? | LP GAS SUPPLY TO ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS778 | COMMON REG STATION OULET PRESS TRANSMITTER ISO. VALVE |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS779 | COMMON REG STATION OULET PRESS TRANSMITTER ISO. VALVE |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS788D | YV-788 DRAIN VALVE |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS785D | YV-785 DRAIN VALVE |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS787 | YV-787 DRAIN VALVE |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS210 | SKID09 hp reg station outlet bypass FG compressor |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS201/883?? | SKID09 HP REG STATION low pressure gas heater isolation |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS876 | 8” LOW FLOW REGULATING STATION INLET |  | HP REGULATING STATION (09) |  | FGS |  | Open
00-VFGS876D | 8” LOW FLOW REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS882 | LOW FLOW NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS890 | LOW FLOW REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS893 | LOW FLOW REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS877 | 8” LOW FLOW REGULATING STATION OUTLET |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS877D | 8” LOW FLOW REGULATING STATION OUTLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS894 | REDUCED GAS HEADER NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS874 | 16” SEC. REGULATING STATION INLET |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS874D | 16” SEC. REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS881 | SEC. REG. STATION NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS889 | SEC. REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS892 | SEC. REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS875 | 16” SEC. REGULATING STATION OUTLET |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS875D | 16” SEC. REGULATING STATION OUTLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS883?? | 6” OUTLET TO ELECTRIC HEATER |  | HP REGULATING STATION (09) |  | FGS |  | Open
00-VFGS872 | 16” PRI. REGULATING STATION INLET |  | HP REGULATING STATION (09) |  | FGS |  | Open
00-VFGS872D | 16” PRI. REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS880 | PRI. REG. STATION NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | Closed
00-VFGS888 | PRI. REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS891 | PRI. REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS873 | 16” PRI. REGULATING STATION OULET |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS873D | 16” PRI. REGULATING STATION OULET DRAIN |  | HP REGULATING STATION (09) |  | FGS
00-VFGS257 | SKID09 HP reg. station outlet to fueal gas compressors |  | HP REGULATING STATION (09) |  | FGS |  | Open
00-VFGS254 | N2 Purge Isolation |  | HP REGULATING STATION (09) |  | FGS |  | Closed
00-VFGS257 | SKID 9 OUTLET TO GAS COMPRESSORS |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS884 | 6" TO ELECTIC HEATER NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS887D | YV-887 DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS878 | REGSTAION SKID 9 OUTLET PRESSURE TRANSMITTER |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS879 | REGSTAION SKID 9 OUTLET PRESSURE TRANSMITTER |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS888D | YV-888 DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS885D | YV-885 DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS901 | LP HEATER GAS NITROGEN PURGE/DRAIN VALVE |  | LP ELECTRIC HEATER |  | FGS |  | CLOSED
00-VFGS278 | Equipment Isolation (ANR/NB to chromatograph) |  | BOP GAS CHROMATOGRAPH |  | FGS |  | OPEN
00-VFGS279 | Equipment Isolation (Mix to chromatograph) |  | BOP GAS CHROMATOGRAPH |  | FGS |  | OPEN
00-VFGS280 | Equipment Isolation (Alliance to chromatograph) |  | BOP GAS CHROMATOGRAPH |  | FGS |  | OPEN
00-VFGS133 | GT Fuel Gas Calorie Meter Sample Tubing Isolation |  | GT FUEL GAS CALORIE METER |  | FGS |  | OPEN
00-VFGS136 | GT Fuel Gas Calorie Meter Sample Vent |  | GT FUEL GAS CALORIE METER |  | FGS |  | CLOSED
00-VFGS137 | GT Fuel Gas Calorie Meter Sample Tubing Isolation |  | GT FUEL GAS CALORIE METER |  | FGS |  | OPEN
00-VFGS202F | FG compressor “A” gas inlet |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS205F | FG compressor “A” gas outlet |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS281 | N2 Purge/vent Isolation (A compressor outlet) |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS476 | GAS COMPRESSOR “A” INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS442A | GAS COMPRESSOR “A” S/U PURGE INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS442B | GAS COMPRESSOR “A” S/U PURGE OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS442C | GAS COMPRESSOR “A” GAS PURGE NITROGEN FILL/DRAIN VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-446 | GAS COMPRESSOR “A” INLET HEADER DRAIN |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-448 | GAS COMPRESSOR “A” GAS SUPPLY TO SEAL FILTER |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-452 | GAS COMPRESSOR “A” DISCHARGE CONTROL VALVE BLEED |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-479 | GAS COMPRESSOR “A” OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-401A | GAS COMPRESSOR “A” SEAL SUPPLY FLOW VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-401B | GAS COMPRESSOR “A” SEAL SUPPLY BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-404 | NITROGEN SUPPLY TO SEAL BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | Open
00-VFGS-424E | GAS COMPRESSOR “A” LUBE OIL FILTER PRESSURE EQUALIZATION VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-424A | GAS COMPRESSOR “A” 227A OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-424G | GAS COMPRESSOR “A” 227B OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-422 | GAS COMPRESSOR “A” CONTROL OIL TO VALVE 00-PSV-FGS-421 ISOLATION |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-423 | GAS COMPRESSOR “A” OIL RESERVOIR DRAIN |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-302 | FG Nitrogen Supply Isolation (A compressor) |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-449A | GAS COMPRESSOR "A" COMPRESSOR DISCHARGE PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-445A | GAS COMPRESSOR "A" COMPRESSOR INLET PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-450A | GAS COMPRESSOR "A" FLOW METER HIGH SIDE ISOLATION |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-450B | GAS COMPRESSOR "A" FLOW METER LOW SIDE ISOLATION |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-400A | GAS COMPRESSOR "A" SEAL GAS SUPPLY FILTER DP TRANSMITTER HIGH SIDE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-400B | GAS COMPRESSOR "A" SEAL GAS SUPPLY FILTER DP TRANSMITTER LOW SIDE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-403A | GAS COMPRESSOR "A" SEAL VENT PRESSURE TRANSMITTER ISOLATION |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-149 | GAS COMPRESSOR "A" LUBE OIL SUPPLY DRAIN |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-148 | GAS COMPRESSOR "A" LUBE OIL RETURN DRAIN |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS203F | FG compressor “B” gas inlet |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
00-VFGS206F | FG compressor “B” gas outlet |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
00-VFGS-282 | N2 Purge/vent Isolation (B compressor outlet) |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” S/U PURGE INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” S/U PURGE OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” GAS PURGE NITROGEN FILL/DRAIN VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” INLET HEADER DRAIN |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” GAS SUPPLY TO SEAL FILTER |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” DISCHARGE CONTROL VALVE BLEED |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” SEAL SUPPLY FLOW VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” SEAL SUPPLY BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| NITROGEN SUPPLY TO SEAL BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | Open
| GAS COMPRESSOR “B” LUBE OIL FILTER PRESSURE EQUALIZATION VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” 227A OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” 227B OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” CONTROL OIL TO VALVE 00-PSV-FGS-421 ISOLATION |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” OIL RESERVOIR DRAIN |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
00-VFGS-303 | FG Nitrogen Supply Isolation (A compressor) |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" COMPRESSOR DISCHARGE PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" COMPRESSOR INLET PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" FLOW METER HIGH SIDE ISOLATION |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" FLOW METER LOW SIDE ISOLATION |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" SEAL GAS SUPPLY FILTER DP TRANSMITTER HIGH SIDE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" SEAL GAS SUPPLY FILTER DP TRANSMITTER LOW SIDE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" SEAL VENT PRESSURE TRANSMITTER ISOLATION |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
00-VFGS-147 | GAS COMPRESSOR "B" LUBE OIL SUPPLY DRAIN |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
00-VFGS-146 | GAS COMPRESSOR "B" LUBE OIL RETURN DRAIN |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
00-VFGS204F | FG compressor “C” gas inlet |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
00-VFGS207F | FG compressor “C” gas outlet |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
00-VFGS283 | N2 Purge/vent Isolation (C compressor outlet) |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” S/U PURGE INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” S/U PURGE OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” GAS PURGE NITROGEN FILL/DRAIN VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” INLET HEADER DRAIN |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” GAS SUPPLY TO SEAL FILTER |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” DISCHARGE CONTROL VALVE BLEED |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” SEAL SUPPLY FLOW VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” SEAL SUPPLY BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| NITROGEN SUPPLY TO SEAL BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | Open
| GAS COMPRESSOR “C” LUBE OIL FILTER PRESSURE EQUALIZATION VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” 227A OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” 227B OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” CONTROL OIL TO VALVE 00-PSV-FGS-421 ISOLATION |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” OIL RESERVOIR DRAIN |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
00-VFGS304 | FG Nitrogen Supply Isolation (A compressor) |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" COMPRESSOR DISCHARGE PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" COMPRESSOR INLET PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" FLOW METER HIGH SIDE ISOLATION |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" FLOW METER LOW SIDE ISOLATION |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" SEAL GAS SUPPLY FILTER DP TRANSMITTER HIGH SIDE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" SEAL GAS SUPPLY FILTER DP TRANSMITTER LOW SIDE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" SEAL VENT PRESSURE TRANSMITTER ISOLATION |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
00-VFGS-147 | GAS COMPRESSOR "C" LUBE OIL SUPPLY DRAIN |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
00-VFGS-146 | GAS COMPRESSOR "C" LUBE OIL RETURN DRAIN |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
00-VFGS-800A | NITROGEN GENERATOR “A” INLET |  | NITROGEN GENERATOR |  | FGS |  | OPEN
00-FCV-FGS800A | NITROGEN GENERATOR “A” OUTLET FLOW CONTROL VALVE |  | NITROGEN GENERATOR |  | FGS |  | THROTTLED
00-VFGS-801A | NITROGEN GENERATOR “A” OUTLET BLOCK VALVE |  | NITROGEN GENERATOR |  | FGS |  | OPEN
00-VFGS-800B | NITROGEN GENERATOR “B” INLET |  | NITROGEN GENERATOR |  | FGS |  | OPEN
00-FCV-FGS-800B | NITROGEN GENERATOR “B” OUTLET FLOW CONTROL VALVE |  | NITROGEN GENERATOR |  | FGS |  | THROTTLED
00-VFGS-801B | NITROGEN GENERATOR “B” OUTLET BLOCK VALVE |  | NITROGEN GENERATOR |  | FGS |  | OPEN
00-VFGS301 | COMON GT GAS HEADER NITROGEN PURGE/VENT |  | COMMON GT HEADER |  | FGS |  | CLOSED
00-VFGS101 | COMON GT GAS HEADER PRESSURE TRANSMITTER ISOLATION |  | COMMON GT HEADER |  | FGS |  | OPEN
00-VFGS102 | COMON GT GAS HEADER PRESSURE TRANSMITTER ISOLATION |  | COMMON GT HEADER |  | FGS |  | OPEN
01-VFGS113 | UNIT 1 GAS FLOW METER INLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS124 | UNIT 1 GAS FLOW METER OUTLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS122 | UNIT 1 GAS FLOW METER BYPASS |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS116 | UNIT 1 GAS FLOW METER VENT |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA801 | UNIT 1 GAS FLOW METER PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA802 | UNIT 1 GAS FLOW METER PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS128 | UNIT 1 GAS PERFORMASE HEATER LT DRAIN VESSEL 1 |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA922 | UPPER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA924 | LOWER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA820 | UPPER TRANSMITTER ISOLATION 01MBP01CL121 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA821 | LOWER TRANSMITTER ISOLATION 01MBP01CL121 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA822 | UPPER TRANSMITTER ISOLATION 01MBPCL122 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA823 | LOWER TRANSMITTER ISOLATION 01MBPCL122 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS134 | UNIT 1 GAS PERFORMASE HEATER DRAIN LT VESSEL 2 |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA932 | UPPER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA934 | LOWER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA830 | UPPER TRANSMITTER ISOLATION 01MBP01CL131 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA831 | LOWER TRANSMITTER ISOLATION 01MBP01CL131 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA832 | UPPER TRANSMITTER ISOLATION 01MBPCL132 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA833 | LOWER TRANSMITTER ISOLATION 01MBPCL132 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS130 | UNIT 1 FUEAL GAS PERFORMANCE HEATER ISOLATION TO AUTOMATIC VENT |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS123 | UNIT 1 BYPASS FUEL GAS PERFORMANCE HEATER VENT VALVE |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS115 | UNIT 1 FUEAL GAS PERFORMANCE HEATER NITROGEN PURGE/VENT |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS174 | UNIT 1 GT FUEL GAS FILTER INLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS192 | UNIT 1 GT FUEL GAS FILTER OUTLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS143 | UNIT 1 GT FUEL GAS FILTER NITROGEN SUPPLY |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS193 | UNIT 1 GT FUEL GAS FILTER INLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA907 | UNIT 1 FILTER DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA908 | UNIT 1 FILTER DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA911 | UNIT 1 FILTER DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA842 | UNIT 1 FILTER DP HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA843 | UNIT 1 FILTER DP HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA844 | UNIT 1 FILTER DP LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA845 | UNIT 1 FILTER DP LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA909 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA910 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA912 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA907 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA908 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA911 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS147 | PRESSURE TRANSMITTER 01MBP01CP110 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS148 | PRESSURE TRANSMITTER 01MBP01CP110 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS157 | PRESSURE TRANSMITTER 01MBP01CP111 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS158 | PRESSURE TRANSMITTER 01MBP01CP111 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS177 | UNIT 1 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS178 | UNIT 1 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS184 | UNIT 1 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP02AA807 | UNIT 1 GAS HEADER INLET PRESSURE TRANSMITTER 01MBP02CP141 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA808 | UNIT 1 GAS HEADER INLET PRESSURE TRANSMITTER 01MBP02CP141 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA801 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP101 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA802 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP101 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA803 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP102 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA804 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP102 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA805 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP103 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA806 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP103 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA825 | UNIT 1 MAIN "A" DP TRANSMITTER 01MBP03CP521 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA826 | UNIT 1 MAIN "A" DP TRANSMITTER 01MBP03CP521 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA827 | UNIT 1 MAIN "A" DP TRANSMITTER 01MBP03CP521 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA828 | UNIT 1 MAIN "A" DP TRANSMITTER 01MBP03CP521 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA821 | UNIT 1 MAIN "A" PRESSURE TRANSMITTER 01MBP03CP136 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA822 | UNIT 1 MAIN "A" PRESSURE TRANSMITTER 01MBP03CP136 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA910 | UNIT 1 MAIN "A" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA911 | UNIT 1 MAIN "A" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA835 | UNIT 1 MAIN "B" DP TRANSMITTER 01MBP03CP531 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA836 | UNIT 1 MAIN "B" DP TRANSMITTER 01MBP03CP531 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA837 | UNIT 1 MAIN "B" DP TRANSMITTER 01MBP03CP531 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA838 | UNIT 1 MAIN "B" DP TRANSMITTER 01MBP03CP531 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA831 | UNIT 1 MAIN "B" PRESSURE TRANSMITTER 01MBP03CP146 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA832 | UNIT 1 MAIN "B" PRESSURE TRANSMITTER 01MBP03CP146 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA920 | UNIT 1 MAIN "B" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA921 | UNIT 1 MAIN "B" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA815 | UNIT 1 PILOT "A" DP TRANSMITTER 01MBP03CP501 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA816 | UNIT 1 PILOT "A" DP TRANSMITTER 01MBP03CP501 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA817 | UNIT 1 PILOT "A" DP TRANSMITTER 01MBP03CP501 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA818 | UNIT 1 PILOT "A" DP TRANSMITTER 01MBP03CP501 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA811 | UNIT 1 PILOT "A" PRESSURE TRANSMITTER 01MBP03CP126 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA812 | UNIT 1 PILOT "A" PRESSURE TRANSMITTER 01MBP03CP126 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA900 | UNIT 1 PILOT "A" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA901 | UNIT 1 PILOT "A" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA845 | UNIT 1 PILOT "B" DP TRANSMITTER 01MBP03CP511 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA846 | UNIT 1 PILOT "B" DP TRANSMITTER 01MBP03CP511 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA847 | UNIT 1 PILOT "B" DP TRANSMITTER 01MBP03CP511 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA848 | UNIT 1 PILOT "B" DP TRANSMITTER 01MBP03CP511 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA841 | UNIT 1 PILOT "B" PRESSURE TRANSMITTER 01MBP03CP156 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA842 | UNIT 1 PILOT "B" PRESSURE TRANSMITTER 01MBP03CP156 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA930 | UNIT 1 PILOT "B" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA931 | UNIT 1 PILOT "B" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA855 | UNIT 1 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA856 | UNIT 1 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA857 | UNIT 1 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA858 | UNIT 1 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA851 | UNIT 1 PILOT TOPHAT PRESSURE TRANSMITTER 01MBP03CP166 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA852 | UNIT 1 PILOT TOPHAT PRESSURE TRANSMITTER 01MBP03CP166 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA940 | UNIT 1 PILOT TOPHAT RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA941 | UNIT 1 PILOT TOPHAT RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
02-VFGS113 | UNIT 2 GAS FLOW METER INLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS124 | UNIT 2 GAS FLOW METER OUTLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS122 | UNIT 2 GAS FLOW METER BYPASS |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS116 | UNIT 2 GAS FLOW METER VENT |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA801 | UNIT 2 GAS FLOW METER PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA802 | UNIT 2 GAS FLOW METER PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS128 | UNIT 2 GAS PERFORMASE HEATER LT DRAIN VESSEL 1 |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP02AA922 | UPPER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA924 | LOWER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA820 | UPPER TRANSMITTER ISOLATION 02MBP01CL121 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA821 | LOWER TRANSMITTER ISOLATION 02MBP01CL121 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA822 | UPPER TRANSMITTER ISOLATION 02MBP01CL122 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA823 | LOWER TRANSMITTER ISOLATION 02MBP01CL122 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS134 | UNIT 2 GAS PERFORMASE HEATER DRAIN LT VESSEL 2 |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP02AA932 | UPPER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA934 | LOWER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA830 | UPPER TRANSMITTER ISOLATION 02MBP01CL131 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA831 | LOWER TRANSMITTER ISOLATION 02MBP01CL131 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA832 | UPPER TRANSMITTER ISOLATION 02MBPCL132 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA833 | LOWER TRANSMITTER ISOLATION 02MBPCL132 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS130 | UNIT 2 FUEAL GAS PERFORMANCE HEATER ISOLATION TO AUTOMATIC VENT |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS123 | UNIT 2 BYPASS FUEL GAS PERFORMANCE HEATER VENT VALVE |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS115 | UNIT 2 FUEAL GAS PERFORMANCE HEATER NITROGEN PURGE/VENT |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS174 | UNIT 2 GT FUEL GAS FILTER INLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS192 | UNIT 2 GT FUEL GAS FILTER OUTLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS143 | UNIT 2 GT FUEL GAS FILTER NITROGEN SUPPLY |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS193 | UNIT 2 GT FUEL GAS FILTER INLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA907 | UNIT 2 FILTER DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA908 | UNIT 2 FILTER DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA911 | UNIT 2 FILTER DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA842 | UNIT 2 FILTER DP HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA843 | UNIT 2 FILTER DP HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA844 | UNIT 2 FILTER DP LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA845 | UNIT 2 FILTER DP LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA909 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA910 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA912 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA907 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA908 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA911 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS147 | PRESSURE TRANSMITTER 02MBP01CP110 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS148 | PRESSURE TRANSMITTER 02MBP01CP110 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS157 | PRESSURE TRANSMITTER 02MBP01CP111 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS158 | PRESSURE TRANSMITTER 02MBP01CP111 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS177 | UNIT 2 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS178 | UNIT 2 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS184 | UNIT 2 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP02AA807 | UNIT 2 GAS HEADER INLET PRESSURE TRANSMITTER 02MBP02CP141 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA808 | UNIT 2 GAS HEADER INLET PRESSURE TRANSMITTER 02MBP02CP141 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA801 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP101 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA802 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP101 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA803 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 02MBP02CP102 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA804 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 02MBP02CP102 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA805 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 02MBP02CP103 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA806 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 02MBP02CP103 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA825 | UNIT 2 MAIN "A" DP TRANSMITTER 02MBP03CP521 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA826 | UNIT 2 MAIN "A" DP TRANSMITTER 02MBP03CP521 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA827 | UNIT 2 MAIN "A" DP TRANSMITTER 02MBP03CP521 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA828 | UNIT 2 MAIN "A" DP TRANSMITTER 02MBP03CP521 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA821 | UNIT 2 MAIN "A" PRESSURE TRANSMITTER 02MBP03CP136 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA822 | UNIT 2 MAIN "A" PRESSURE TRANSMITTER 02MBP03CP136 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA910 | UNIT 2 MAIN "A" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA911 | UNIT 2 MAIN "A" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA835 | UNIT 2 MAIN "B" DP TRANSMITTER 02MBP03CP531 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA836 | UNIT 2 MAIN "B" DP TRANSMITTER 02MBP03CP531 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA837 | UNIT 2 MAIN "B" DP TRANSMITTER 02MBP03CP531 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA838 | UNIT 2 MAIN "B" DP TRANSMITTER 02MBP03CP531 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA831 | UNIT 2 MAIN "B" PRESSURE TRANSMITTER 02MBP03CP146 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA832 | UNIT 2 MAIN "B" PRESSURE TRANSMITTER 02MBP03CP146 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA920 | UNIT 2 MAIN "B" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA921 | UNIT 2 MAIN "B" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA815 | UNIT 2 PILOT "A" DP TRANSMITTER 02MBP03CP501 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA816 | UNIT 2 PILOT "A" DP TRANSMITTER 02MBP03CP501 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA817 | UNIT 2 PILOT "A" DP TRANSMITTER 02MBP03CP501 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA818 | UNIT 2 PILOT "A" DP TRANSMITTER 02MBP03CP501 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA811 | UNIT 2 PILOT "A" PRESSURE TRANSMITTER 02MBP03CP126 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA812 | UNIT 2 PILOT "A" PRESSURE TRANSMITTER 02MBP03CP126 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA900 | UNIT 2 PILOT "A" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA902 | UNIT 2 PILOT "A" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA845 | UNIT 2 PILOT "B" DP TRANSMITTER 02MBP03CP511 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA846 | UNIT 2 PILOT "B" DP TRANSMITTER 02MBP03CP511 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA847 | UNIT 2 PILOT "B" DP TRANSMITTER 02MBP03CP511 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA848 | UNIT 2 PILOT "B" DP TRANSMITTER 02MBP03CP511 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA841 | UNIT 2 PILOT "B" PRESSURE TRANSMITTER 02MBP03CP156 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA842 | UNIT 2 PILOT "B" PRESSURE TRANSMITTER 02MBP03CP156 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA930 | UNIT 2 PILOT "B" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA931 | UNIT 2 PILOT "B" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA855 | UNIT 2 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA856 | UNIT 2 PILOT TOPHAT DP TRANSMITTER 02MBP03CP541 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA857 | UNIT 2 PILOT TOPHAT DP TRANSMITTER 02MBP03CP541 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA858 | UNIT 2 PILOT TOPHAT DP TRANSMITTER 02MBP03CP541 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA851 | UNIT 2 PILOT TOPHAT PRESSURE TRANSMITTER 02MBP03CP166 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA852 | UNIT 2 PILOT TOPHAT PRESSURE TRANSMITTER 02MBP03CP166 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA940 | UNIT 2 PILOT TOPHAT RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA941 | UNIT 2 PILOT TOPHAT RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
00-VFGS300 | Common header nitrogen purge/vent |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS227 | AUX BOILER REGULATION SKID ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS309 | AUX BOILER REG STATION VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS310 | BUILDING HEAT SUPPLY HEADER VENT BEFORE ISOLATOIN |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS264 | BUILDING HEAT GAS SUPPLY ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS311 | AUX BUILDING HEAT SUPPLY HEADER VENT BEFORE ISOLATOIN |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS265 | AUX BUILDING HEAT GAS SUPPLY ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS-YV-905 | DRAIN VALVE FOR YV-905 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS906 | AUX BOILER HEADER DRAIN BEFORE CONTROL VLV |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS908 | PRESSURE TRANSMITER ISOLATION INNERSTAGE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS909 | PRESSURE TRANSMITER ISOLATION INNERSTAGE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS915 | AUX BOILER INNERSTAGE PRESSURE REGULATION VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS911 | PRESSURE TRANSMITER ISOLATION AFTER REGULATION VALVE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS914 | PRESSURE TRANSMITER ISOLATION AFTER REGULATION VALVE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS312 | AUX BOILER HEADER NITROGEN PURGE/VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS228 | AUX BOILER GAS SUPPLY ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS917 | SUPPLY PRESSURE TRANSMITTER BUILDING HEAT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS913 | SUPPLY PRESSURE TRANSMITTER BUILDING HEAT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS904 | ORDERIZER RAW GAS SUPPLY ISOLATION TO ODORIZER PANEL |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGSXXX | ORDERIZER ORDERANT SUPPLY ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGSXXX | ORDERISER PANEL ORDERIZED GAS OUTLET |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGSXXX | ORDERIZER INJECTION POINT ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS912 | ORDERIZED GAS TO AUX BOILER BUILDING DRAIN BEFORE REGULATING VALVE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS920 | ORDERIZED GAS TO AUX BOILER BUILDING DRAIN INNERSTAGE REGULATING VALVE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
01-VFGS244 | UNIT 1 TURBINE BUILDING GAS ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
02-VFGS241 | UNIT 2 TURBINE BUILDING GAS ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
01-VFGS941 | UNIT 1 TURBINE BUILING SUPPLY INTERSTAGE REGULATION VALVE VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
01-VFGS946 | UNIT 1 TURBINE BUILING HEAT REGULATION VALVE ISOLATION PCV-946 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
01-VFGS950 | UNIT 1 TURBINE BUILING HEAT REGULATION VALVE ISOLATION PCV-950 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS272 | UNIT 1 TURBINE BUILDING HEAT REGULATION SKID OUTLET |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS313 | UNIT 1 TURBINE BUILDING HEAT REGULATION SKID VENT BEFORE REGULATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS314 | UNIT 1 TURBINE BUILDING HEAT REGULATION SKID VENT AFTER REGULATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
02-VFGS941 | UNIT 2 TURBINE BUILING SUPPLY INTERSTAGE REGULATION VALVE VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
02-VFGS946 | UNIT 2 TURBINE BUILING HEAT REGULATION VALVE ISOLATION PCV-946 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
02-VFGS950 | UNIT 2 TURBINE BUILING HEAT REGULATION VALVE ISOLATION PCV-950 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS273 | UNIT 2 TURBINE BUILDING HEAT REGULATION SKID OUTLET |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS315 | UNIT 2 TURBINE BUILDING HEAT REGULATION SKID VENT BEFORE REGULATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS316 | UNIT 2 TURBINE BUILDING HEAT REGULATION SKID VENT AFTER REGULATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
01-VFGS176 | UNIT 1 DUCT BURNER REGULATION SKID ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS217 | UNIT 1 DUCT BURNER SKID VENT AFTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS-YV-922 | DRAIN ON STOP VALVE YV-922 |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-VFGS923 | UNIT 1 DUCT BURNER DRAIN BEFORE PRESSURE CONTROL VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-VFGS932 | UNIT 1 DUCT BURNER INTERSTAGE VENT |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-VFGS925 | UNIT 1 DUCT BURNER INNERSTAGE PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS926 | UNIT 1 DUCT BURNER INNERSTAGE PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS928 | UNIT 1 DUCT BURNER PRESSURE TRANSMITTER ISOLATION AFTER REGULATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS929 | UNIT 1 DUCT BURNER PRESSURE TRANSMITTER ISOLATION AFTER REGULATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS179 | UNIT 1 DUCT BURNER PRESSURE REGULATION OUTLET |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS120 | UNIT 1 DUCT BURNER SUPPLY VENT AFTER REGULATION SKID |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR800 | DUCT BURNER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR803 | GAS FLOW INDICATING TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR804 | GAS FLOW INDICATING TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR810 | PURGE ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR811 | PRESSURE INDCATING TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR812 | PRESSURE INDCATING TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR820 | PRESSURE INDICATION TRANSMITTER AFTER STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR845 | DRAIN AFTER STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR827 | DP TRANSMITTER HIGH SIDE STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR828 | DP TRANSMITTER LOW SIDE STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR846 | DUCT BURNER HEADER DRAIN |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR835 | PRESSURE AFTER CONTROL VALVE TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR836 | PRESSURE AFTER CONTROL VALVE TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-FG-V-0942 | DRAIN AFTER FLOW CONTROL VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR860 | PILOT GAS SUPPLY ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR866 | PILOT GAS PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR886 | PILIOT HEADER DRAIN BETWEEN PRIMARY STOP VALVES |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR870 | PILOT HEADER STOP VALVE PRESSURE DP HIGH SIDE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR871 | PILOT HEADER STOP VALVE PRESSURE DP LOW SIDE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR887 | PILOT HEADER DRAIN BETWEEN STOP VALVES SECONDARY |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-FG-V-0943 | PILOT HEADER DRAIN AFTER LAST STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR955 | FLAME SCANNER BLOWER DISCHARGE PRESSURE TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR956 | FLAME SCANNER BLOWER DISCHARGE PRESSURE TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BURXXX | FLAME SCANNER BLOWER DISCHARGE DRAIN VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
02-VFGS176 | UNIT 2 DUCT BURNER REGULATION SKID ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS217 | UNIT 2 DUCT BURNER SKID VENT AFTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS-YV-922 | DRAIN ON STOP VALVE YV-922 |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-VFGS923 | UNIT 2 DUCT BURNER DRAIN BEFORE PRESSURE CONTROL VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-VFGS932 | UNIT 2 DUCT BURNER INTERSTAGE VENT |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-VFGS925 | UNIT 2 DUCT BURNER INNERSTAGE PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS926 | UNIT 2 DUCT BURNER INNERSTAGE PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS928 | UNIT 2 DUCT BURNER PRESSURE TRANSMITTER ISOLATION AFTER REGULATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS929 | UNIT 2 DUCT BURNER PRESSURE TRANSMITTER ISOLATION AFTER REGULATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS179 | UNIT 2 DUCT BURNER PRESSURE REGULATION OUTLET |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS120 | UNIT 2 DUCT BURNER SUPPLY VENT AFTER REGULATION SKID |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR800 | DUCT BURNER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR803 | GAS FLOW INDICATING TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR804 | GAS FLOW INDICATING TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR810 | PURGE ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR811 | PRESSURE INDCATING TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR812 | PRESSURE INDCATING TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR820 | PRESSURE INDICATION TRANSMITTER AFTER STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR845 | DRAIN AFTER STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR827 | DP TRANSMITTER HIGH SIDE STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR828 | DP TRANSMITTER LOW SIDE STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR846 | DUCT BURNER HEADER DRAIN |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR835 | PRESSURE AFTER CONTROL VALVE TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR836 | PRESSURE AFTER CONTROL VALVE TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-FG-V-0942 | DRAIN AFTER FLOW CONTROL VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR860 | PILOT GAS SUPPLY ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR866 | PILOT GAS PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR886 | PILIOT HEADER DRAIN BETWEEN PRIMARY STOP VALVES |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR870 | PILOT HEADER STOP VALVE PRESSURE DP HIGH SIDE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR871 | PILOT HEADER STOP VALVE PRESSURE DP LOW SIDE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR887 | PILOT HEADER DRAIN BETWEEN STOP VALVES SECONDARY |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-FG-V-0943 | PILOT HEADER DRAIN AFTER LAST STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR955 | FLAME SCANNER BLOWER DISCHARGE PRESSURE TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR956 | FLAME SCANNER BLOWER DISCHARGE PRESSURE TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BURXXX | FLAME SCANNER BLOWER DISCHARGE DRAIN VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED

## Sheet2
Location | Equipment | Type | System
ACC lower
ACC upper
LRVP area
CRT area
CRT landing
ST Drains Tank area
ST lower East
ST lower
ST upper East
HRSG uppew SW
HRSG lower SW
HRSG upper NW
HRSG lower NW
HRSG upper SE
HRSG lower SE
HRSG upper SW
HRSG lower SE
Pipe Rack 1st
Pipe Rack 2nd
Pipe Rack 3rd
HRSG West landing
HRSG East landing
HRSG BD tank area
Aux Boiler Room
345 kV Swithcyard
GCB landing
Metering Skid area
Fuel Gas fenced area
Coalessing filter area
Regulating skid area
Warehouse 2/3 area
WW sump area
Water Treatment
Ammonia storage tank area
SW/DW storage tank area
Fire pump enclosure
Maintenance shop
Server Room

## Sheet3
ID | Description | Location | Equipment | Type | System | P&ID | Normal Pos | Iso Pos
IV-863A | LIT863A (upper iso) | CRT landing | LIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-863C | LIT863B (upper iso) | CRT landing | LIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-863E | LIT863C (upper iso) | CRT landing | LIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-864A | Level Gauge 864 (upper iso) | CRT landing | LIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-867A | PIT867A iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-867B | PIT867B iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-867C | PIT867C iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-866 | PIT866 iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
IV-868 | PIT868 iso | CRT landing | PIT | Iso Vlv | CND | 94.03.40.100.02-PD-0001-00 (4of13) | OPEN | CLOSED
VCND216 | Condensate Recirc before CV | CRT landing | CV/CRT | Iso Vlv | CND | 20023894-PD-053A | OPEN | CLOSED
VCND132 | Condensate Recirc after CV | CRT landing | CV/CRT | Iso Vlv | CND | 20023894-PD-053A | OPEN | CLOSED
VCND217 | Condensate Recirc CV bypass | CRT landing | CV/CRT | Iso Vlv | CND | 20023894-PD-053A | OPEN | CLOSED
FCV-CND331 | Condensate Recirc CV | CRT landing | CRT | AOCV | CND | 20023894-PD-053A | CLOSED | CLOSED
VCND 378 | Condensate Recirc Vent (after CV) | CRT landing | CRT | Drain/Vent Vlv | CND | 20023894-PD-053A | CLOSED | OPEN
VCND 152 | Condensate Recirc Drain (after CV) | CRT landing | CRT | Drain/Vent Vlv | CND | 20023894-PD-053A | CLOSED | OPEN
VCND 379 | Condensate Recirc Vent (after strainer) | CRT landing | CRT | Drain/Vent Vlv | CND | 20023894-PD-053A | CLOSED | OPEN
VBFW 213 | BFP "A" HP FW recirc vent after strainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 214 | BFP "A" HP FW recirc vent after strainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW | BFP "A" HP FW recirc iso before CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW 218 | BFP "A" HP FW recirc iso after CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW 230 | BFP "B" HP FW recirc vent after strainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 231 | BFP "B" HP FW recirc vent after strainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW | BFP "B" HP FW recirc iso before CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW239 | BFP "B" HP FW recirc iso after CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW 322 | From TCA to CRT vent after srtainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 323 | From TCA to CRT vent after srtainer | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW | From TCA to CRT before CV iso | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW339 | From TCA to CRT after CV iso | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VBFW 459 | FGPH to receiver tank after strainer vent | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 460 | FGPH to receiver tank after strainer vent | CRT landing | CRT | Drain/Vent Vlv | BFW |  | CLOSED | OPEN
VBFW 379 | FGPH to receiver tank iso after CV | CRT landing | CV/CRT | Iso Vlv | BFW |  | OPEN | CLOSED
VDWS 638 | Normal makeup Iso before and after CV | CRT landing | CRT | Iso Vlv | DWS |  | OPEN | CLOSED
VDWS 639 | Normal makeup Iso before and after CV | CRT landing | CRT | Iso Vlv | DWS |  | OPEN | CLOSED
VDWS 641/642 | Emergency makeup Iso before and after CV | CRT landing | CRT | Iso Vlv | DWS |  | OPEN
VDWS 636 | Makeup CV bypass | CRT landing | CRT | Iso Vlv | DWS |  | CLOSED
VDWS 648 | Normal makeup drain | CRT landing | CRT | Drain/Vent Vlv | DWS |  | CLOSED
VDWS 105 | Normal makeup vent | CRT landing | CRT | Drain/Vent Vlv | DWS |  | CLOSED
VDWS 643 | Emergency makeup drain | CRT landing | CRT | Drain/Vent Vlv | DWS |  | CLOSED
VDWS532F/534F | Emergency makeup FT | CRT landing | FIT | Iso Vlv | DWS |  | OPEN
VDWS528F/530F | Normal makeup FT | CRT landing | FIT | Iso Vlv | DWS |  | OPEN
VAXS174/175 | Steam to air ejector CV iso | CRT landing | CRT/Air ejector | Iso Vlv | AXS |  | OPEN
VAXS153 | Steam to air ejector drain | CRT landing | CRT/Air ejector | Drain/Vent Vlv | AXS |  | CLOSED
VAXS152 | Steam to air ejector CV bypass | CRT landing | CRT/Air ejector | Iso Vlv | AXS |  | CLOSED
VAXS186 | Air ejector PIT iso | CRT landing | PIT | Iso Vlv | AXS |  | OPEN
VAXS183 | Air ejector vent | CRT landing | CRT/Air ejector | Drain/Vent Vlv | AXS |  | CLOSED
| Air ejector suction/discharge | CRT landing | CRT/Air ejector | Iso Vlv | AXS
VAXS168/165 | Sparging steam CV iso | CRT landing | CRT | Iso Vlv | AXS |  | OPEN
VAXS147 | Sparging steam strainer drain | CRT landing | CRT | Drain/Vent Vlv | AXS |  | CLOSED
VAXS182 | Sparging steam strainer vent | CRT landing | CRT | Drain/Vent Vlv | AXS |  | CLOSED
VAXS102/122 | Sparging steam strainer PDIT | CRT landing | CRT | Iso Vlv | AXS |  | OPEN
VAXS145 | Sparging steam CV bypass | CRT landing | CRT | Iso Vlv | AXS |  | CLOSED
VCND106 | ST DT pump discharge Vent | CRT landing | CRT | Drain/Vent Vlv | CND |  | CLOSED
VCND259 | ST DT pump discharge Drain | CRT landing | CRT | Drain/Vent Vlv | CND |  | CLOSED
VCND258 | ST DT pump discharge Vent | CRT landing | CRT | Drain/Vent Vlv | CND |  | CLOSED
VCND | Condensate Receiver Tank drain valve | CRT area | CRT |  | CND |  | CLOSED
VCND | Level indicating instruments (4 lower valves) | CRT area | LIT |  | CND |  | OPEN
| Cond. Receiver Tank PITs | CRT area | PIT |  | CND |  | OPEN
VCND 377 | Condensate Recirc Drain (after strainer) | CRT area | CRT |  | CND |  | CLOSED
VCND 404 | Condensate Recirc Strainer Vent | CRT area | CRT |  | CND |  | CLOSED
VCND 195 | Condensate Recirc Strainer Drain | CRT area | CRT |  | CND |  | CLOSED
VCND 323 | Condensate Recirc Strainer isolation | CRT area | CRT |  | CND |  | OPEN
VCND | Condensate Recirc Strainer DP isolation (2) valves | CRT area | CRT |  | CND |  | OPEN
VCND577 | ACC east loop seal drain | CRT area | ACC |  | CND |  | CLOSED
VCND576 | ACC west loop seal drain | CRT area | ACC |  | CND |  | CLOSED
| ACC street iso bypass trap (2 sets) | CRT area | ACC |  | CND |  | CLOSED
VBFW 381/415 | BFP "A" HP FW recirc drain after strainer | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 215 | BFP "A" HP FW strainer iso | CRT area | Strainer |  | BFW |  | OPEN
VBFW 216/217 | BFP "A" HP FW strainer drain | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 411/412 | BFP "A" HP FW strainer vent | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 232 | BFP "B" HP FW strainer iso | CRT area | Strainer |  | BFW |  | OPEN
VBFW 233/234 | BFP "B" HP FW strainer drain | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 427/428 | BFP "B" HP FW strainer vent | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 338/365 | BFP "B" HP FW recirc drain after strainer | CRT area | CRT |  | BFW |  | CLOSED
VBFW 330/922 | From TCA to Cond. Receiver Tank iso (2) vlvs | CRT area | CRT |  | BFW |  | OPEN
VBFW 165/166 | From TCA to Cond. Receiver Tank drain | CRT area | CRT |  | BFW |  | CLOSED
VBFW 923/532 | From TCA to Cond. Receiver Tank strainer vent | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 333/334 | From TCA to Cond. Receiver Tank strainer drain | CRT area | Strainer |  | BFW |  | CLOSED
VBFW305/306 | From TCA to Cond. Receiver Tank drain after strainer | CRT area | Strainer |  | BFW |  | OPEN
VBFW 290/361 | Gas performance heater to receiver tank iso (2) valves | CRT area |  |  | BFW |  | OPEN
VBFW 402/403 | Gas performance heater to receiver tank drain | CRT area |  |  | BFW |  | CLOSED
VBFW 440/441 | Gas performance heater to receiver tank strainer vent | CRT area | Strainer |  | BFW |  | CLOSED
VBFW 292/366 | Gas performance heater to receiver tank strainer drain | CRT area | Strainer |  | BFW |  | CLOSED
VBFW449/450 | Gas performance heater to receiver tank after strainer drain | CRT area |  |  | BFW |  | CLOSED
VAXS117/201 | Steam trap iso | CRT area |  |  | AXS
VAXS120 | Steam trap bypass | CRT area |  |  | AXS
VAXS119 | Steam trap strainer drain | CRT area |  |  | AXS
VAXS200 | Steam trap drain | CRT area |  |  | AXS
VCND | Inlet valve to strainer #1 | CRT area | CND pump A |  | CND |  | OPEN
VCND | Inlet valve to strainer #2 | CRT area | CND pump A |  | CND |  | CLOSED
VCND | Outlet valve from strainer 1 | CRT area | CND pump A |  | CND |  | OPEN
VCND | Outlet valve from strainer 2 | CRT area | CND pump A |  | CND |  | CLOSED
VCND 166/171 | Strainer Drain valves (2) | CRT area | CND pump A |  | CND |  | CLOSED
VCND 191/320/118/100 | Strainer Vent valves (4) | CRT area | CND pump A |  | CND |  | CLOSED
VCND 179/142 | DP transmitter isolation (2) valves | CRT area | CND pump A |  | CND |  | OPEN
VCND 143 | CND pump suction pressure gauge isolation. | CRT area | CND pump A |  | CND |  | OPEN
VCND 128 | CND Pump Discharge valve | CRT area | CND pump A |  | CND |  | OPEN
VCND 128 | CND Pump Discharge bypass valve | CRT area | CND pump A |  | CND |  | CLOSED
VCND 128 | CND Pump Discharge equalizing valve | CRT area | CND pump A |  | CND |  | OPEN
VCND 818 | Seal supply valve | CRT area | CND pump A |  | CND |  | OPEN
VCND 157/814 | Air vent valve | CRT area | CND pump A |  | CND |  | CLOSED
VCND 820 | Equalizing valve | CRT area | CND pump A |  | CND |  | OPEN
VCND 819 | Seal water pressure gauge | CRT area | CND pump A |  | CND |  | OPEN
VCND 804 | Pump discharge pressure gauge | CRT area | CND pump A |  | CND |  | OPEN
VCND 104 | Pump Discharge pressure transmitter | CRT area | CND pump A |  | CND |  | OPEN
VCND 196 | Pump Discharge Drain | CRT area | CND pump A |  | CND |  | CLOSED
VCND | Inlet valve to strainer 1 | CRT area | CND pump B |  | CND |  | OPEN
VCND | Inlet valve to strainer 2 | CRT area | CND pump B |  | CND |  | CLOSED
VCND | Outlet valve from strainer 1 | CRT area | CND pump B |  | CND |  | OPEN
VCND | Outlet valve from strainer 2 | CRT area | CND pump B |  | CND |  | CLOSED
VCND 361/176 | Strainer Drain valves (2) | CRT area | CND pump B |  | CND |  | CLOSED
154/360/135/129 | Strainer Vent valves (4) | CRT area | CND pump B |  | CND |  | CLOSED
VCND 181/164 | DP transmitter isolation (2) valves | CRT area | CND pump B |  | CND |  | OPEN
VCND 183 | CND pump suction pressure gauge isolation. | CRT area | CND pump B |  | CND |  | OPEN
VCND 194 | CND Pump Discharge valve | CRT area | CND pump B |  | CND
VCND 194 | CND Pump Discharge bypass valve | CRT area | CND pump B |  | CND |  | CLOSED
VCND 194 | CND Pump Discharge equalizing valve | CRT area | CND pump B |  | CND |  | OPEN
VCND 848 | Seal supply valve | CRT area | CND pump B |  | CND |  | OPEN
VCND 333/844 | Air vent valve (2) | CRT area | CND pump B |  | CND |  | CLOSED
VCND 850 | Equalizing valve | CRT area | CND pump B |  | CND |  | OPEN
VCND 846 | Seal water pressure gauge | CRT area | CND pump B |  | CND |  | OPEN
VCND 834 | Pump discharge pressure gauge | CRT area | CND pump B |  | CND |  | OPEN
VCND 137 | Pump Discharge pressure transmitter | CRT area | CND pump B |  | CND |  | OPEN
VCND 167 | Pump Discharge Drain | CRT area | CND pump B |  | CND |  | CLOSED
VCND | Inlet valve to strainer 1 | CRT area | CND pump C |  | CND |  | OPEN
VCND | Inlet valve to strainer 2 | CRT area | CND pump C |  | CND |  | CLOSED
VCND | Outlet valve from strainer 1 | CRT area | CND pump C |  | CND |  | OPEN
VCND | Outlet valve from strainer 2 | CRT area | CND pump C |  | CND |  | CLOSED
VCND 173/178 | Strainer Drain valves (2) | CRT area | CND pump C |  | CND |  | CLOSED
VCND 330/133/168/165 | Strainer Vent valves (4) | CRT area | CND pump C |  | CND |  | CLOSED
VCND 112/192 | DP transmitter isolation (2) valves | CRT area | CND pump C |  | CND |  | OPEN
VCND 131 | CND pump suction pressure gauge isolation. | CRT area | CND pump C |  | CND |  | OPEN
VCND 329 | CND Pump Discharge valve | CRT area | CND pump C |  | CND
VCND 329 | CND Pump Discharge bypass valve | CRT area | CND pump C |  | CND |  | CLOSED
VCND 329 | CND Pump Discharge equalizing valve | CRT area | CND pump C |  | CND |  | OPEN
VCND 878 | Seal supply valve | CRT area | CND pump C |  | CND |  | OPEN
VCND 113/874 | Air vent valve | CRT area | CND pump C |  | CND |  | CLOSED
VCND 880 | Equalizing valve | CRT area | CND pump C |  | CND |  | OPEN
VCND 876 | Seal water pressure gauge | CRT area | CND pump C |  | CND |  | OPEN
VCND 864 | Pump discharge pressure gauge | CRT area | CND pump C |  | CND |  | OPEN
VCND 130 | Pump Discharge pressure transmitter | CRT area | CND pump C |  | CND |  | OPEN
VCND 189 | Pump Discharge Drain | CRT area | CND pump C |  | CND |  | CLOSED
VCND238/236 | Demin Water supply valves | CRT area | CND header |  | CND
VCND 237 | Demin Water drain | CRT area | CND header |  | CND |  | CLOSED
VCND 127 | Common Condensate Discharge Header Vent | CRT area | CND header |  | CND |  | CLOSED
VCND 151 | Common Condensate Discharge Header PIT | CRT area | PIT |  | CND |  | OPEN
VCND 201 | Filter Inlet MOV equalizing valve | CRT area | IRON Filer A |  | CND |  | OPEN
VCND 172 | Filter Outlet | CRT area | IRON Filer A |  | CND |  | OPEN
VCND 172 | Filter Outlet Bypass Valve | CRT area | IRON Filer A |  | CND |  | CLOSED
VCND 172 | Filter Outlet Equalizing Valve | CRT area | IRON Filer A |  | CND |  | OPEN
VCND 139 | Filter Vent | CRT area | IRON Filer A |  | CND |  | CLOSED
VCND 114/144 | Filter Drains (2) | CRT area | IRON Filer A |  | CND |  | CLOSED
VCND 184/177 | Filter D/P Transmitter (2) isolation valves | CRT area | IRON Filer A |  | CND |  | OPEN
VCND 211 | Filter Inlet MOV equalizing valve | CRT area | IRON Filer B |  | CND |  | OPEN
VCND 174 | Filter Outlet | CRT area | IRON Filer B |  | CND |  | OPEN
VCND 174 | Filter Outlet Bypass Valve | CRT area | IRON Filer B |  | CND |  | CLOSED
VCND 174 | Filter Outlet Equalizing Valve | CRT area | IRON Filer B |  | CND |  | OPEN
VCND 140 | Filter Vent | CRT area | IRON Filer B |  | CND |  | CLOSED
VCND 101/362 | Filter Drains (2) | CRT area | IRON Filer B |  | CND |  | CLOSED
VCND 187/180 | Filter D/P Transmitter (2) isolation valves | CRT area | IRON Filer B |  | CND |  | OPEN
VCND 160 | Before MOV isolation valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 160 | Before MOV bypass valve | CRT area | IRON Filter Bypass |  | CND |  | CLOSED
VCND 160 | Before MOV equalizing valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 221 | MOV Equalizing valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 163 | After MOV isolation valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 163 | After MOV equalizing valve | CRT area | IRON Filter Bypass |  | CND |  | OPEN
VCND 163 | After MOV bypass valve | CRT area | IRON Filter Bypass |  | CND |  | CLOSED
VCND 188 | Iron Filter Bypass line drain | CRT area | IRON Filter Bypass |  | CND |  | CLOSED
VCND | Vent Before Iron Filters | CRT area | IRON Filter Bypass |  | CND |  | CLOSED
VCND272 | Drains tank pumps seal water iso | ST Drains Tank area | ST DT pump |  | CND |  | OPEN
VCND273 | Drains tank pumps seal water drain | ST Drains Tank area | ST DT pump |  | CND |  | CLOSED
| Steam Duct Drip Leg LT iso (6 valves) | ST Drains Tank area | ST DT pump
VSTP 165 | DT pmup A discharge | ST Drains Tank area | ST DT pump |  | VSTP |  | OPEN
VSTP 178 | DT pmup B discharge | ST Drains Tank area | ST DT pump |  | VSTP |  | OPEN
VSTP 166 | DT pump common discharge iso | ST Drains Tank area | ST DT pump |  | VSTP |  | OPEN
| Drains tank sump pump A | ST Drains Tank area | ST DT pump |  | VSTP
| Drains tank sump pump B | ST Drains Tank area | ST DT pump |  | VSTP
VCND 198/367 | HP Drains Tank spray CV iso | ST Drains Tank area | HP DT |  | CND |  | OPEN
VCND 366 | HP Drains Tank spray CV bypass | ST Drains Tank area | HP DT |  | CND |  | CLOSED
VCND 200 | HP Drains Tank spray supply drain | ST Drains Tank area | HP DT |  | CND |  | CLOSED
VSTP 195/196/111/112/134/135 | HP DT Level Transmitters | ST Drains Tank area | LT |  | STP |  | OPEN
VSTP 110 | HP DT PIT | ST Drains Tank area | PT |  | STP |  | OPEN
VSTP 116 | HP DT Drain | ST Drains Tank area | HP DT |  | STP |  | CLOSED
VSTP 113/115 | HP DT Drain to LP DT CV iso | ST Drains Tank area | HP DT |  | STP |  | OPEN
VSTP 370/371 | HP DT Drain to LP DT CV iso | ST Drains Tank area | HP DT |  | STP |  | OPEN
VSTP 114 | HP DT Drain before CV | ST Drains Tank area | HP DT |  | STP |  | CLOSED
VSTP 130 | HP DT Drain before CV | ST Drains Tank area | HP DT |  | STP |  | CLOSED
VSTP 141 | LP DT PIT | ST Drains Tank area | PT |  | STP |  | OPEN
VSTP 143/144/148/149/150/151 | LP DT LT | ST Drains Tank area | LT |  | STP |  | OPEN
VSTP 152 | LP DT drain | ST Drains Tank area | LP DT |  | STP |  | CLOSED
VCND 214/261 | LP Drains Tank spray CV iso | ST Drains Tank area | LP DT |  | STP |  | OPEN
VCND 262 | LP Drains Tank spray CV bypass | ST Drains Tank area | LP DT |  | STP |  | CLOSED
VCND 215 | LP Drains Tank spray supply drain | ST Drains Tank area | LP DT |  | STP |  | CLOSED
VSTP 155/156 | DT pump A suction strainer PDT | ST Drains Tank area | PT |  | STP |  | OPEN
VSTP 118/158 | DT pump A suction drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 117/157 | DT pump A suction vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 161 | DT pmup A vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VCND 279/280 | DT pmup A seal supply | ST Drains Tank area | ST DT pump |  | STP |  | OPEN
VSTP 164 | DT pmup A discharge drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 168/169 | DT pump B suction strainer PDT | ST Drains Tank area | ST DT pump |  | STP |  | OPEN
VSTP 124/171 | DT pump B suction drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 126/170 | DT pump B suction vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 174 | DT pmup B vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VCND 244/245 | DT pmup B seal supply | ST Drains Tank area | ST DT pump |  | STP |  | OPEN
VSTP 177 | DT pmup B discharge drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 386 | DT pump discharge vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 106/258 | DT pump discharge vent | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VSTP 259 | DT pump discharge drain | ST Drains Tank area | ST DT pump |  | STP |  | CLOSED
VCND190/175/308/124 | Flow Transmitter (4 valves) | ST upper East | FT |  | CND |  | OPEN
VCND138 | Vent before Gland Steam Condenser | ST upper East | GS condenser |  | CND |  | CLOSED
VCND146 | Local Pressure Gauge | ST upper East | GS condenser |  | CND |  | OPEN
VCND402/403 | Gland Steam Condenser drains (in and out) | ST upper East | GS condenser |  | CND |  | CLOSED
VCND400/401 | Gland Steam Condenser vents (in and out) | ST upper East | GS condenser |  | CND |  | CLOSED
VCND193 | Local Pressure Gauge after GSC | ST upper East | GS condenser |  | CND |  | OPEN
VCND225 | Strainer #1 inlet isolation | ST upper East | Strainer |  | CND |  | OPEN
VCND228 | Strainer #2 inlet isolation | ST upper East | Strainer |  | CND |  | CLOSED
VCND227 | Strainer #1 outlet isolation | ST upper East | Strainer |  | CND |  | OPEN
VCND230 | Strainer #2 outlet isolation | ST upper East | Strainer |  | CND |  | CLOSED
VCND233/234 | Strainer DP isolation valves (2) | ST upper East | Strainer |  | CND |  | OPEN
VCND226/229 | Strainer Drain valves (2) | ST upper East | Strainer |  | CND |  | CLOSED
VCND231/232 | Strainer Vent valves (2) | ST upper East | Strainer |  | CND |  | CLOSED
VCND | Hood Spray and Gland Steam attemperator | ST upper East | Attemperator |  | CND |  | OPEN
VCND271 | Hood spray strainer drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND126/145 | Hood spray FCV isolation valves (2) | ST upper East | Attemperator |  | CND |  | OPEN
VCND147 | Hood spray FCV bypass valve | ST upper East | Attemperator |  | CND |  | CLOSED
VCND123 | Hood spray local gauge | ST upper East | Attemperator |  | CND |  | OPEN
VCND186 | Hood spray vent | ST upper East | Attemperator |  | CND |  | CLOSED
VCND201 | Gland steam attemperator isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND406 | Gland steam attemperator strainer drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND207/209 | Gland steam attemperator flow transmitter (2) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND211 | Gland steam attemperator drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND212 | Gland steam attemperator isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND134 | Curtain spray isolation valve | ST upper East | Attemperator |  | CND |  | OPEN
VCND321/322 | Curtain spray flow transmitter (2) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND324/326 | Curtain spray FCV isolation valves (2) | ST upper East | Attemperator |  | CND |  | OPEN
VCND327 | Curtain spray FCV bypass valve | ST upper East | Attemperator |  | CND |  | CLOSED
VCND328 | Curtain spray PIT | ST upper East | Attemperator |  | CND |  | OPEN
VCND405 | Curtain spray vent | ST upper East | Attemperator |  | CND |  | CLOSED
VCND221 | LP Bypass spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND156/169 | LP Bypass spray flow transmitter (2) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND158 | LP Bypass spray drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND141 | LP Bypass spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND105 | LP Bypass spray drain (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | Attemperator |  | CND |  | CLOSED
VCND223 | CRH ventilator spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND159/162 | CRH ventilator spray Flow transmitter (2) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND108 | CRH ventilator spray drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND109 | CRH ventilator spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND110/216 | CRH ventilator spray vent (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | Attemperator |  | CND |  | CLOSED
VCND363/364 | CRH ventilator spray drain (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | Attemperator |  | CND |  | CLOSED
VCND224 | HRH spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND125/170/301/302 | HRH spray flow transmitter (4) valves | ST upper East | Attemperator |  | CND |  | OPEN
VCND116 | HRH spray drain | ST upper East | Attemperator |  | CND |  | CLOSED
VCND119 | HRH spray isolation | ST upper East | Attemperator |  | CND |  | OPEN
VCND307 | HRH spray vent | ST upper East | Attemperator |  | CND |  | CLOSED
VCND260 | HRH spray dray (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | Attemperator |  | CND |  | CLOSED
VBFW614/615 | TCA return to Cond.Receiv. Vent | ST upper East | TCA |  | BFW |  | CLOSED
MAW01AA001 | GS Exhauster A inlet | ST upper East | GS condenser |  | STP
MAW01AA002 | GS Exhauster B inlet | ST upper East | GS condenser |  | STP
VSTP 125 | GS Exhauster A outlet | ST upper East | GS condenser |  | STP
VSTP 179 | GS Exhauster B outlet | ST upper East | GS condenser |  | STP
VAXS 196/197/198 | GS supply drain valves | ST upper East | GS condenser |  | STP
VSTP 148/149 | GS supply CV isolations | ST upper East | GS condenser |  | STP
VSTP204 | GS supply CV bypass | ST upper East | GS condenser |  | STP
VSTP105 | HP SV/CV seat drain | ST upper East | ST |  | STP
VSTP107 | HRH SV/CV seat drain AOV iso | ST upper East | ST |  | STP
VCRH 131 | Ventilator CV manual iso. | ST upper East | ST |  | CRH
VCRH 102/103/141/142 | Ventilator line PITs (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | ST |  | CRH
VHRH 113/114 | HRH Bypass warm up line vent | ST upper East | ST |  | HRH
VHRH 116 | HRH Bypass warm up line iso | ST upper East | ST |  | HRH
VHRH 125/126 | HRH Bypass line PITs (OUTSIDE DECK) | ST upper East (OUTSIDE DECK) | ST |  | HRH
| Condenser Vacuum PITs (127/128/129) | ST upper East | PT
VCND 501/502/503 | LP turbine exhause pressure PITs | ST upper East | ST |  | CND
01-VAXS 132 | Aux steam header vent (stmr bldg) | ST upper East | Aux Steam Header |  | AXS
01-VAXS 190 | Drain before steam trap | ST upper East | Steam Trap |  | AXS
01-VAXS 191/194 | Steam trap iso | ST upper East | Steam Trap |  | AXS
01-VAXS 202 | Steam Trap bypass | ST upper East | Steam Trap |  | AXS
01-VAXS 195 | Steam Trap strainer drain | ST upper East | Steam Trap |  | AXS
VSTP 119 | GSC drain to funnel | ST lower East | GS condenser |  | STP
VSTP 120/121 | GSC drain isolation before and after trap | ST lower East | GS condenser |  | STP
VSTP 123 | GSC drain trap bypass | ST lower East | GS condenser |  | STP
VSTP 137 | GSC drain trap vent back to GSC | ST lower East | GS condenser |  | STP
VSTP 122 | GSC drain trap strainer drain | ST lower East | GS condenser |  | STP
VSTP 146/147/153/154 | GS Exhauster drains | ST lower East | GS condenser |  | STP
VAX 159 | GS supply iso before superheater | ST lower East | Gland Steam |  | STP
VAXS 101 | GS supply vent before superheater | ST lower East | Gland Steam |  | STP
VAXS 104/105 | GS superheater drain trap | ST lower East | Gland Steam |  | STP
VAXS 107 | GS superheater drain trap bypass | ST lower East | Gland Steam |  | STP
VAXS 106 | GS superheater drain trap strainer drain | ST lower East | Gland Steam |  | STP
VSTP 159/181 | GS mist separator orphis drain | ST lower | Gland Steam |  | STP
VSTP 167 | GS mist separator orphis bypass | ST lower | Gland Steam |  | STP
VSTP 182 | GS mist separator common drain | ST lower | Gland Steam |  | STP
VSTP 131/133 | GS header PT | ST lower | PT |  | STP
VSTP 183/184/185 | GS header drain | ST lower | Gland Steam |  | STP
VSTP 127/129 | GS spill over CV iso | ST lower | Gland Steam |  | STP
VSTP 132 | GS spill over CV bypass | ST lower | Gland Steam |  | STP
VSTP 139/140 | Seals/stem leak off to GSC drain | ST lower | Gland Steam |  | STP
VLPS 142/167 | 2 pressure transmitters (before stop) | ST lower | PT |  | LPS
VLPS 164/152 | Drains on LP steam Bypass line | ST lower East |  |  | LPS
VLPS 101/103/104/106 | Bypass line Drip leg level Isolations | ST lower East |  |  | LPS
VLPS 108/111 | Bypass line Drip leg level drains | ST lower East |  |  | LPS
VLPS 109 | LP steam Bypass drip leg CV isolation | ST lower East |  |  | LPS
| LP steam PIT (turbine side) | ST lower |  |  | LPS
VLPS 163 | LP steam header vent (before drip leg) | ST lower |  |  | LPS
VLPS 169/170/171/172 | LP steam Drip Leg level swithc iso | ST lower |  |  | LPS
VLPS 174/175/176/177 | Vents and drains on level switches | ST lower |  |  | LPS
VLPS 149/150 | Drip leg drans | ST lower |  |  | LPS
VLPS 151 | Drip leg CV iso | ST lower |  |  | LPS
VLPS 173 | LP header vent after strainer | ST lower |  |  | LPS
VLPS | LP steam strainer drain | ST lower |  |  | LPS
VLPS | Manuall iso drain before and after LP steam CV | ST lower |  |  | LPS
MAC03 AA801 | LP Turbine inlet steam PIT (123) | ST lower |  |  | LPS
VHPS 100/101/102/103 | HPS header PITs (outside steamer bldg) | ST lower East |  |  | HPS
VHPS 106/107 | HPS header vent | ST lower East |  |  | HPS
VHPS108 | HPS header Drip Leg manual isolation | ST lower East |  |  | HPS
VHPS109/110 | HPS header Drip Leg drain | ST lower East |  |  | HPS
VSTP104 | HPS after seat drain | ST lower |  |  | HPS
MAA03 AA801/802/803/804/805/806 | HP turbine inlet steam PITs (101/102/103) | ST lower East |  |  | HPS
MAA41 AA801/802/803 | HP turbine exhaust PITs (110/111/112) | ST lower East |  |  | CRH
VCRH 128/143 | HP turbine exhaust PIT | ST lower East |  |  | CRH
VCRH 139/144 | HP turbine exhaust vent | ST lower East |  |  | CRH
VCRH 102/103/141/142 | Ventilator line PITs | ST lower |  |  | CRH
VCRH 108/109/175/177/110/112/176/178 | HP turbine exhaust Drip Leg Level Switches | ST lower East |  |  | CRH
VCRH 101/151/125/150 | HP turbine exhaust Drip Leg Level Switche drains | ST lower East |  |  | CRH
VCRH129/145/126/149 | HP turbine exhaust Drip Leg Level Switche vents | ST lower East |  |  | CRH
VCRH 127 | HP turbine exhaust Drip Leg AOV iso | ST lower East |  |  | CRH
VCRH 133/134 | CRH Drip Leg drain | ST lower East |  |  | CRH
VCRH 104/105/106/107/154/155/156/157 | CRH Drip Leg Level Switches | ST lower East |  |  | CRH
VCRH158/160/161/123 | CRH Drip Leg Level Switche drains | ST lower East |  |  | CRH
VCRH 152/116/153/113 | CRH Drip Leg Level Switche vents | ST lower East |  |  | CRH
VCRH 130 | CRH Drip Leg AOV iso | ST lower East |  |  | CRH
VCRH 135/138 | CRH Drip Leg drain | ST lower East |  |  | CRH
VHRH 115 | HRH Bypass warm up line iso (overhead) | ST lower East |  |  | HRH
VHRH 111/105 | HRH Bypass warm up line vent | ST lower East |  |  | HRH
VHRH 110 | HRH dripleg before SV/CV AOV iso | ST lower East |  |  | HRH
VHRH 120/137 | HRH dripleg drain | ST lower East |  |  | HRH
VSTP106 | HRH after seat drain AOV iso | ST lower East |  |  | HRH
VHRH 100/102/103/104/121/106 | HRH PITs (before stop) | ST lower East |  |  | HRH
MAB03 BR801/802/803 | IP Turbine Inlet steam PITs (113/114/115) | ST lower East |  |  | HRH
VHHS 803/804/805/806/807/808/809/810 | 1st stage HP superheater Drip leg 2 Lvl switches (8) isolation valves | HRSG lower East |  |  | HHS
VHHS 867/868 | 1st stage HP superheater Drip leg drain (2) valves | HRSG lower East |  |  | HHS
VHHS 811/812 | HP Superheater vent to atmoshpere | HRSG lower East |  |  | HHS
VHHS 909/910 | 3rd stage HP superheater Drip leg drain (2) valves | HRSG lower East |  |  | HHS
VHRS 969/970 | Reheater interstage Dripleg drain | HRSG lower West |  |  | HRS
VHIS 856/857 | IP superheater outlet dripleg drain | HRSG lower |  |  | HIS
VHIS 987/988 | IP superheater outlet PIT | HRSG lower |  |  | HIS
VHIS 864/865/866/867/994/995/996/997 | IP steam flow meter | HRSG lower |  |  | HIS
VHIS 801/802 | IP superheater outlet drain (before MOV) | HRSG lower |  |  | HIS
VHIS 908 | IP superheater outlet MOV bypass | HRSG lower |  |  | HIS
VHIS 858/859 | IP steam Header drain (after MOV) | HRSG lower |  |  | HIS
VHLS 811/812/813/814/815/816 | 3 PIT (6) iso valves | HRSG lower West |  |  | HLS
VHLS 808/809 | Sampling | HRSG lower West |  |  | HLS
VHLS 986/987 | Drip leg drain before MOV | HRSG lower West |  |  | HLS
01-VAXS 189/290 | Steam to HP Evap Steam trap ISOs | HRSG lower |  |  | AXS
01-VAXS 289 | Steam to HP Evap Steam trap bypass | HRSG lower |  |  | AXS
01-VAXS 144 | Steam to HP Evap Steam trap strainer drain | HRSG lower |  |  | AXS
01-VAXS 291 | Steam to HP Evap drain before steam trap | HRSG lower |  |  | AXS
VHHS 904 | Steam to HP Evap MOV bypass | HRSG lower |  |  | HHS
VHHS 994/995 | Steam to HP Evap drain after MOV | HRSG lower |  |  | HHS
VHHS 996/997 | Steam to HP Evap strainer drain | HRSG lower |  |  | HHS
01-VHIS 852/853 | Steam to IP Evap strainer drain | HRSG lower |  |  | HIS
01-VHLS 904 | Steam to LP Evap MOV bypass | HRSG lower |  |  | HLS
01-VHLS 985/999 | Steam to LP Evap drain after MOV | HRSG lower |  |  | HLS
01-VHLS 992/993 | Steam to LP Evap strainer drain | HRSG lower |  |  | HLS
01-VAXS 135/136 | Steam to LP Evap Steam trap iso | HRSG lower |  |  | AXS
01-VAXS 138 | Steam to LP Evap Steam trap bypass | HRSG lower |  |  | AXS
01-VAXS 137 | Steam to LP Evap Steam trap strainer drain | HRSG lower |  |  | AXS
01-VAXS 113 | Steam to LP Evap Drain before Steam trap | HRSG lower |  |  | AXS
01-VAXS 155 | Drain before steam trap | HRSG lower NE |  |  | AXS
01-VAXS 112/115 | Steam trap iso | HRSG lower NE |  |  | AXS
01-VAXS 129 | Steam Trap bypass | HRSG lower NE |  |  | AXS
01-VAXS 116 | Steam Trap strainer drain | HRSG lower NE |  |  | AXS
01-VAXS 130 | Drain before steam trap | HRSG lower East |  |  | AXS
01-VAXS 103/161 | Steam trap iso | HRSG lower East |  |  | AXS
01-VAXS 164 | Steam Trap bypass | HRSG lower East |  |  | AXS
01-VAXS 160 | Steam Trap strainer drain | HRSG lower East |  |  | AXS
01-VAXS 199 | Drain before steam trap | HRSG lower West |  |  | AXS
01-VAXS 166/118 | Steam trap iso | HRSG lower West |  |  | AXS
01-VAXS 167 | Steam Trap bypass | HRSG lower West |  |  | AXS
01-VAXS 203 | Steam Trap strainer drain | HRSG lower West |  |  | AXS
VHHS 916/917 | HP FW to economizer PIT (before LCV) |  |  |  | BFW HP |  | OPEN
VHHS 907 | HP drum LCV bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS 901 | HP drum High flow LCV iso | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS | HP drum High flow LCV iso bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | HP drum High flow LCV iso equalizing valve | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 903 | HP drum Low flow LCV iso | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS | HP drum Low flow LCV iso bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | HP drum Low flow LCV iso equalizing valve | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 857/856 | HP drum High flow drain | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS 859/858 | HP drum Low flow drain | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS 902 | HP drum High flow LCV outlet iso | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS | HP drum High flow LCV outlet iso bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | HP drum High flow LCV outlet iso equalizing | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 904 | HP drum Low flow LCV outlet iso | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS | HP drum Low flow LCV outlet iso bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | HP drum Low flow LCV outlet iso equalizing | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 913/912 | HP drum FW drain before MOV | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | MOV 901 bypass | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS | MOV 901 equalizing | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 914/915 | HP economizer inlet PIT (after LCV) | HRSG lower West |  |  | BFW HP |  | OPEN
VHHS 961/929/930/931/932/933/934/935/936/937 | HP economizer drain root valves | HRSG lower West |  |  | BFW HP |  | CLOSED
VHHS 900/906/938/905 | HP economizer drain block valves | HRSG lower West |  |  | BFW HP |  | CLOSED
VBFW 303/304 | FW to TCA drain before cooler | HRSG lower West |  |  | BFW HP |  | CLOSED
VBFW 700/701/929/928 | PDI across TCA | HRSG lower West |  |  | BFW HP |  | OPEN
VBFW 305/294 | Drain After TCA coller | HRSG lower West |  |  | BFW HP |  | CLOSED
VHIS 901 | IP Economizer Inlet Isolation | HRSG lower |  |  | BFW IP
VHIS 901 | IP Economizer Inlet Isolation bypass | HRSG lower |  |  | BFW IP
VHIS 901 | IP Economizer Inlet Isolation equalizing valve | HRSG lower |  |  | BFW IP
VHIS 919/920 | IP Economizer inlet drain valves (2) | HRSG lower |  |  | BFW IP
VHIS | IP Economizer inlet MOV bypass | HRSG lower |  |  | BFW IP
VHIS | IP Economizer inlet MOV equalizing valve | HRSG lower |  |  | BFW IP
VHIS 904 | IP fill line isolation | HRSG lower |  |  | BFW IP
VHIS 906/907 | IP Economizer Inlet PIT isolation (2) valves | HRSG lower |  |  | BFW IP
VHIS 910/911/912 | IP Economizer Drains (Root) | HRSG lower |  |  | BFW IP
VHIS 913 | IP Economizer Drain (Block) | HRSG lower |  |  | BFW IP
VBFW 918/919/820/821/822/823/824/825 | (2) Flow transmitters (8) valves |  |  |  | BFW IP |  | OPEN
VBFW 960/961 | Drain before CV |  |  |  | BFW IP |  | CLOSED
VBFW 848/849 | Strainer Drain (2) valves |  |  |  | BFW IP |  | CLOSED
VBFW 826/827/828/829 | Strainer DPT (4) valves |  |  |  | BFW IP |  | OPEN
VBFW 930 | After CV iso |  |  |  | BFW IP |  | OPEN
VBFW 962/963 | Drain after check (2) valves |  |  |  | BFW IP |  | CLOSED
VBFW 394F/159F/160F | BFP "A" suction PIT iso (3) (at the pump) | HRSG lower West |  |  | BFW |  | OPEN
| BFP "A" CCW inlet/outlet | HRSG lower West |  |  | BFW
VBFW 180F/179F/395F | BFP "B" suction PIT iso (3) | HRSG lower West |  |  | BFW |  | OPEN
| BFP "B" CCW inlet/outlet | HRSG lower West |  |  | BFW
VCND336/375 | Condensate header pressure transmitters | HRSG lower NW |  |  | CND |  | OPEN
VCND103 | Condensate Dump isolation | HRSG lower NW |  |  | CND |  | CLOSED
VCND153 | Drain before condensate dump CV | HRSG lower NW |  |  | CND |  | CLOSED
VCND337/338 | LP economizer pressure transmitters | HRSG lower NW |  |  | CND |  | OPEN
VHLS902/903 | Drain before LP Economizer inlet MOV | HRSG lower NW |  |  | CND |  | CLOSED
VHLS | MOV bypass | HRSG lower NW |  |  | CND |  | CLOSED
VHLS803/804 | Pressure Transmitter isolations | HRSG lower NW |  |  | CND |  | OPEN
VHLS904 | Cold Condensate inlet isolation | HRSG lower NE |  |  | CND |  | OPEN
VHLS907 | Cold Condensate outlet isolation | HRSG lower NE |  |  | CND |  | OPEN
VHLS905 | Hot Condensate inlet isolation | HRSG lower NE |  |  | CND |  | OPEN
VHLS908 | Hot Condensate outlet isolation | HRSG lower NE |  |  | CND |  | OPEN
VHLS909 | Cold Condensate bypass around heat exchanger | HRSG lower NE |  |  | CND |  | CLOSED
VHLS851/852 | Cold Condensate outlet vent | HRSG lower NE |  |  | CND |  | CLOSED
VHLS829/830 | Cold condensate drain | HRSG lower NE |  |  | CND |  | CLOSED
VHLS801/802 | Drain after Heat Exchanger | HRSG lower NE |  |  | CND |  | CLOSED
VHLS807/810 | Drain after Heat Exchanger | HRSG lower NE |  |  | CND |  | CLOSED
VHLS821/823/824 | LP Economizer Drains (Block) | HRSG lower NW |  |  | CND |  | CLOSED
VHLS 913/916/918/920 | LP Economizer Drains (Root) | HRSG lower NW |  |  | CND |  | CLOSED
VCND352 | To ECA isolation | HRSG SE | ECA |  | CND |  | OPEN
VCND349 | Drain before FCV | HRSG SE | ECA |  | CND |  | OPEN
VCND410 | Vent after FCV | HRSG SE | ECA |  | CND |  | OPEN
VCND311 | ECA pump “A” suction valve | HRSG SE | ECA |  | CND |  | OPEN
VCND313 | ECA pump “B” suction valve | HRSG SE | ECA |  | CND |  | OPEN
VCND359 | ECA pump “A” discharge valve | HRSG SE | ECA |  | CND |  | OPEN
VCND314 | ECA pump “B” discharge valve | HRSG SE | ECA |  | CND |  | OPEN
VCND357/342 | ECA pump “A” DP | HRSG SE | ECA |  | CND |  | OPEN
| ECA pump “A” drain | HRSG SE | ECA |  | CND |  | CLOSED
| ECA pump “B” drain | HRSG SE | ECA |  | CND |  | CLOSED
VCND312/315 | ECA pump “B” DP | HRSG SE | ECA |  | CND |  | OPEN
VCND411 | ECA pump discharge vent | HRSG SE | ECA |  | CND |  | CLOSED
VCND335 | Pressure transmitter | HRSG SE | ECA |  | CND |  | OPEN
VCND197 | 2C cooler drain | HRSG SE | ECA |  | CND |  | CLOSED
VCND210 | 2C cooler vent | HRSG SE | ECA |  | CND |  | CLOSED
VCND240 | ECA cooler pressure transmitter | HRSG SE | ECA |  | CND |  | OPEN
VCND341 | ECA cooler drain | HRSG SE | ECA |  | CND |  | CLOSED
VCND407 | ECA cooler vent | HRSG SE | ECA |  | CND |  | CLOSED
VCND344 | ECA cooler pressure transmitter | HRSG SE | ECA |  | CND |  | OPEN
VCND408 | ECA drain | HRSG SE | ECA |  | CND |  | CLOSED
VCND243 | Isolation to 3-way valve | HRSG SE | ECA |  | CND |  | OPEN
VCND343 | To condensate system isolation | HRSG SE | ECA |  | CND |  | OPEN
VCND348 | Drain after FCV | HRSG SE | ECA |  | CND |  | CLOSED
VCND340 | Isolation after FCV | HRSG SE | ECA |  | CND |  | OPEN
VHBD 9806/9805 | LT iso | HRSG NE | BDT |  | HBD
VHBD 9902/9903 | LG drain | HRSG NE | BDT |  | HBD
VHBD 9804/9805 | LG iso | HRSG NE | BDT |  | HBD
VHBD 9802 | PIT | HRSG NE | BDT |  | HBD
VHBD 9904/9905 | BDT Quenching CV iso | HRSG NE | BDT |  | HBD
VHBD 9906 | BDT Quenching CV bypass | HRSG NE | BDT |  | HBD
VHBD 9907/9908 | BDT Quenching line drain | HRSG NE | BDT |  | HBD
VHBD 9901 | BD tank drain | HRSG NE | BDT |  | HBD
VSWS 100 | BD tank sump pump flush water | HRSG NE | BDT |  | HBD
VSWS 124 | BD tank sump A pump discharge | HRSG NE | BDT |  | HBD
VSWS 123 | BD tank sump B pump discharge | HRSG NE | BDT |  | HBD
VSWS 112 | BD tank sump pump discharge vent | HRSG NE | BDT |  | HBD
VBND 100/101 | BD tank sump pump discharge FT | HRSG NE | BDT |  | HBD
VSWS 101/102 | SW to BDT flow meter | HRSG NE | BDT |  | HBD
VSWS 111 | SW to BDT quenching iso | HRSG NE | BDT |  | HBD
VSWS 108 | SW to BDT quenching drain | HRSG NE | BDT |  | HBD
VSWS 109 | SW to HRSG sump pit quenching iso | HRSG NE | BDT |  | HBD
VSWS 110 | SW to HRSG sump pit quenching drain | HRSG NE | BDT |  | HBD
| HP/IP/LP intermittent blowdown drains | HRSG NE | BDT |  | HBD
VBDN687 | HRSGs sump discharge to WW sump | HRSG NE | BDT |  | HBD
VBDN 688/689 | HRSGs sump discharge to WW sump vent/drain | HRSG NE | BDT |  | HBD
VBDN 613 | HRSGs sump discharge to SW tank | HRSG NE | BDT |  | HBD
VBDN 614/615 | HRSGs sump discharge to SW tank vent/drain | HRSG NE | BDT |  | HBD
| IP continuous BD manual regulator (BD tank) | HRSG NE | BDT |  | HBD
| LP/IP/HP intermitent BD drains (in the pit) | HRSG NE | BDT |  | HBD
01-VAXS 133 | Steam to IP Evap vent | HRSG lower | HRSG |  | AXS
01-VHIS 909 | Steam to IP Evap MOV bypass | HRSG lower | HRSG |  | AXS
01-VHIS 860/861 | Steam to IP Evap drain after MOV | HRSG lower | HRSG |  | AXS
VHS 982/983 | IP superheater outlet sampl | HRSG lower | Sample
VBFW 211/212 | FW to HP interstage atemperator drain | HRSG West Landing | Attemperator HP |  |  |  | CLOSED
VHHS-830/831/832/833/834/835/836/837 | FW to HP interstage atemperator (2) flow transmitters | HRSG West Landing | Attemperator HP |  |  |  | OPEN
VHHS-863/864 | FW to HP interstage atemperator drain (2) valves | HRSG West Landing | Attemperator HP |  |  |  | CLOSED
VHHS-838/839/840/841 | FW to HP interstage atemperator strainer DP | HRSG West Landing | Attemperator HP |  |  |  | OPEN
VHHS-842/843 | FW to HP interstage atemperator strainer drain valve | HRSG West Landing | Attemperator HP |  |  |  | CLOSED
VHHS-844 | FW to HP interstage atemperator iso | HRSG West Landing | Attemperator HP |  |  |  | OPEN
VHHS-865/866 | FW to HP interstage atemperator vent | HRSG West Landing | Attemperator HP |  |  |  | CLOSED
VBFW265 | BFP "A" suction iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW 394F/159F/160F | BFP "A" suction PIT iso (3) (at the pump) | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW 404/405 | BFP "A" HP discharge PIT iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW406/407 | BFP "A" IP discharge PIT iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW 430/506 | BFP "A" IP FW discharge vent (2) valve | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFW269 | BFP "A" IP FW discharge iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
| BFP "A" IP FW discharge iso bypass | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
| BFP "A" IP FW discharge iso equalizing valve | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW 168/169 | BFP "A" IP FW discharge drain | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFV | BFP "A" IP FW discharge MOV equalizing valve | Pipe Rack 1st | BFP A |  | BFW
|  | Pipe Rack 1st | BFP A |  | BFW
VBFW 181/182/183/184/185/186/187/188 | BFP "A" HP FW flow meter iso (8) valves | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFV 189/190 | BFP "A" HP FW discharge vent (2) valves | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFV 192/193 | BFP "A" HP FW discharge drain (2) valves | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFV 271 | BFP "A" HP FW discharge iso | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFV 271 | BFP "A" HP FW discharge iso equalizing valve | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFV 271 | BFP "A" HP FW discharge iso bypass | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
V B F W 604/605 | BFP "A" HP FW discharge vent (2) valves | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VBFW 194/195 | BFP "A" HP FW discharge drain (2) valves | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
| BFP "A" HP FW discharge MOV equalizing valve | Pipe Rack 1st | BFP A |  | BFW |  | OPEN
VBFW147/150 | BFP "A" HP FW recirc vent (second pipe rack) | Pipe Rack 2nd | BFP A |  | BFW |  | CLOSED
VBFW 138/139 | BFP "A" HP FW recirc drain (under first pipe rack) | Pipe Rack 1st | BFP A |  | BFW |  | CLOSED
VHLS 924 | BFP suction iso | one level down under LP drum | BFP A/B suction |  | BFW |  | OPEN
VBFW 149 | BFP suction header drain | Pipe Rack 1st | BFP A/B suction |  | BFW |  | CLOSED
VBFW152 | BFP suction iso | Pipe Rack 1st | BFP A/B suction |  | BFW |  | OPEN
VBFW132 | BFP suction PIT iso | Pipe Rack 1st | BFP A/B suction |  | BFW |  | OPEN
VBFW154/155 | BFP suction strainer DPT | Pipe Rack 1st | BFP A/B suction |  | BFW |  | OPEN
VBFW | BFP suction strainer blowdown | Pipe Rack 1st | BFP A/B suction |  | BFW |  | CLOSED
VBFW 264 | BFP suction from condensate | Pipe Rack 1st | BFP A/B suction |  | BFW |  | OPEN
VBFW266 | BFP "B" suction iso | Pipe Rack 1st | BFP B |  | BFW |  | OPEN
VBFW 180F/179F/395F | BFP "B" suction PIT iso (3) | Pipe Rack 1st | BFP B |  | BFW |  | OPEN
VBFW 177/178 | BFP "B" HP discharge PIT iso | Pipe Rack 1st | BFP B |  | BFW |  | OPEN
VBFW 170/171 | BFP "B" IP discharge PIT iso | Pipe Rack 1st | BFP B |  | BFW IP |  | OPEN
VBFW 172/173 | BFP "B" IP FW discharge vent (2) valve | Pipe Rack 1st | BFP B |  | BFW IP |  | CLOSED
VBFW 270 | BFP "B" IP FW discharge iso | Pipe Rack 1st | BFP B |  | BFW IP |  | OPEN
VBFW | BFP "B" IP FW discharge iso bypass | Pipe Rack 1st | BFP B |  | BFW IP |  | CLOSED
VBFW | BFP "B" IP FW discharge iso equalizing valve | Pipe Rack 1st | BFP B |  | BFW IP |  | OPEN
VBFW 175/176 | BFP "B" IP FW discharge drain | Pipe Rack 1st | BFP B |  | BFW IP |  | CLOSED
| BFP "B" IP FW discharge MOV equalizing valve | Pipe Rack 1st | BFP B |  | BFW IP |  | OPEN
VBFW 219/220/221/222/223/224/225/226 | BFP "B" HP FW flow meter iso (8) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | OPEN
VBFW 227/228 | BFP "B" HP FW discharge vent (2) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 235/236 | BFP "B" HP FW discharge drain (2) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 272 | BFP "B" HP FW discharge iso | Pipe Rack 1st | BFP B |  | BFW HP |  | OPEN
VBFW | BFP "B" HP FW discharge iso equalizing valve | Pipe Rack 1st | BFP B |  | BFW HP |  | OPEN
VBFW | BFP "B" HP FW discharge iso bypass | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 606/607 | BFP "B" HP FW discharge vent (2) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 237/238 | BFP "B" HP FW discharge drain (2) valves | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW | BFP "B" HP FW discharge MOV equalizing valve | Pipe Rack 1st | BFP B |  | BFW HP |  | OPEN
VBFW 209/210 | BFP "B" HP FW recirc vent (second pipe rack) | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 267/337 | BFP "B" HP FW recirc drain (under first pipe rack) | Pipe Rack 1st | BFP B |  | BFW HP |  | CLOSED
VBFW 416/417 | IP FW header Vent | Pipe Rack 1st | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 918 | IP economizer Vent | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 915/917 | IP Economizer Vents (Root) | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 922/923 | FW to IP drum PIT (2) iso valves | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 924/925/926/927/928/929/930/931 | FW to IP drum FT (8) iso valves, 2 transmitters | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 934 | FW to IP drum before CV isolation | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 934 | FW to IP drum before CV isolation bypass | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 934 | FW to IP drum before CV isolation equalizing | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 936 | FW to IP drum CV bypass | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 935 | FW to IP drum after CV isolation | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 935 | FW to IP drum after CV isolation bypass | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 935 | FW to IP drum after CV isolation equalizing | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | OPEN
VHIS 933/932 | Drain before CV | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 854/855 | Drain before CV Iso valve | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 937/938 | Drain after CV | HRSG upper | HRSG/ IP Drum |  | BFW IP |  | CLOSED
VHIS 992 | Phosphate injection iso | HRSG upper West | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 950/951/952/953 | Level Transmitter | HRSG upper West | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 939/940/993/979 | Level Element | HRSG upper West | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS | Level Gauge (2) valves | HRSG upper West | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 941/942/944 | Level instrumnt blowdown | HRSG upper West | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 954/955/956/957/958/959/960/961 | Level Transmitter (8) iso valves, 2 transmitters | HRSG upper East | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 943/948/947/949 | Level Element | HRSG upper East | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS | Level Gauge | HRSG upper East | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 945/946 | Level instrumnt blowdown | HRSG upper East | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 846/847/849/850/851/976/977 | 4 vents to atmosphere (8) iso valves | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 963/964/965/966 | IP drum (2) PIT (4) iso valves | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 971 | Nitrogen Fill iso | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 967/968/969/970 | Nitrogen (2) PIT (4) iso valves | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 998/999 | Pegging steam to LP drum vent (2) iso valves | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 978 | Pegging steam to LP drum iso | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 978 | Pegging steam to LP drum iso bypass | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 978 | Pegging steam to LP drum iso equalizing | Top of the IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 973/974 | IP drum water sample (2) valves | Under IP drum | HRSG/ IP Drum |  | HIS |  | OPEN
VHIS 852/853 | IP sparging steam strainer drain (2) valves (under HRSG) | HRSG lower West | HRSG/ IP Drum |  | HIS |  | CLOSED
VHIS 860/861 | IP sparging steam drain (2) valves | HRSG lower West | HRSG/ IP Drum |  | HIS |  | CLOSED
VBFW 199 | HP BFW PIT to the HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VBFW 200 | HP BFW PIT to the HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VBFW 116 | Drain after HP cold fill iso | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VBFW 608 | HP BFW header to HRSG vent | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VBFW 609 | HP BFW header to HRSG vent | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VHHS 918F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 919F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 920F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 921F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 922F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 923F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 924F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VHHS 925F | HP BFW (2) flow transmitters to HRSG | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | OPEN
VBFW 422 | HP BFW header drain (2) valves | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VBFW 423 | HP BFW header drain (2) valves | Pipe Rack 1st | HRSG/HP Drum |  | BFW HP |  | CLOSED
VHHS 939/940/941/942/943/944/945/946 | HP economizer vent root valves | HRSG upper | HRSG/ HP Drum |  | BFW HP |  | CLOSED
VHHS 947 | HP economizer vent root valve | HRSG upper | HRSG/ HP Drum |  | BFW HP |  | OPEN
VHHS 988 | Phosphate injection iso | HRSG upper West | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 967/968/969/970 | Level Transmitter (4) valves | HRSG upper West | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 963/964/986/987 | Level Element (4) valves | HRSG upper West | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS | Level Gauge (2) valves | HRSG upper West | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 965/966/972 | Level instruments blowdown | HRSG upper West | HRSG/ HP Drum |  | HHS |  | CLOSED
VHHS 991/992 | HP drum water sample (2) valves | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 904 | HP continuous blowdown iso | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS | HP continuous blowdown regulator | HRSG upper East | HRSG/ HP Drum |  | HHS
VHHS 975/976/977/978/979/980/981/982 | (2)Level Transmitters (8) valves | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 971/983/984/985 | Level Element (4) valves | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS | Level Gauge (2) valves | HRSG upper East | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 973/974 | Level instruments blowdown | HRSG upper East | HRSG/ HP Drum |  | HHS |  | CLOSED
VHHS 959 | Nitrogen Fill iso | Top of the HP drum | HRSG/ HP Drum |  | HHS |  | CLOSED
VHHS 956/957 | Nitrogen PIT (2) valves | Top of the HP drum | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 950/951/952/953 | (2) HP Drum PIT (4) valves | Top of the HP drum | HRSG/ HP Drum |  | HHS |  | OPEN
VHHS 801/802 | HP drum vent (2) valves | Top of the HP drum | HRSG/ HP Drum |  | HHS |  | CLOSED
VHHS 998/999 | HP saturated steam sample (2) valves (under HP drum) | Top of the HP drum |  |  | HHS |  | OPEN
VHHS 996/997 | HP sparging steam strainer drain (2) valves (under HRSG) | Top of the HP drum |  |  | HHS |  | CLOSED
VBFW 375/521 | FW to HP terminal atemperator strainer #1 inlet | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 523/555 | FW to HP terminal atemperator strainer #1 outlet | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 246/247 | FW to HP terminal atemperator strainer #1 vent | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 380/509 | FW to HP terminal atemperator strainer #1 drain | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 549/376 | FW to HP terminal atemperator strainer #2 inet | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 383/525 | FW to HP terminal atemperator strainer #2 outlet | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 248/249 | FW to HP terminal atemperator strainer #2 vent | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 503/377 | FW to HP terminal atemperator strainer #2 drain | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 242/243/244/245 | FW to HP terminal atemperator strainer PDIT | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 385F/507F/533F/515F/117F/120F/121F/122F | FW to HP terminal atemperator (3) Flow meters | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 563/565 | FW to HP terminal atemperator vent after flow meters | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 545/547 | FW to HP terminal atemperator drain after block valve | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 531/505 | FW to HP terminal atemperator iso after CV | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | OPEN
VBFW 529/553 | FW to HP terminal atemperator drain | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 240/241 | FW to HP terminal atemperator drain after check valve | Pipe Rack 1st | Attemperator HP |  | BFW HP |  | CLOSED
VBFW 438/424 | IP FW header PIT | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | OPEN
VBFW 106/111 | IP FW strainer #1 inlet iso | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | OPEN
VBFW 107/108 | IP FW strainer #1 outlet iso | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | OPEN
VBFW 101/115 | IP FW strainer #1 drain | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 151/161 | IP FW strainer #1 vent | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 388/105 | IP FW strainer #2 inlet iso | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 391/109 | IP FW strainer #2 outlet iso | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 113/390 | IP FW strainer #2 drain | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 162/163 | IP FW strainer #2 vent | Pipe Rack 1st | Attemperator/Strainer |  | BFW IP |  | CLOSED
VBFW 128/129 | HP steam bypass spray CV iso | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | OPEN
VBFW 130/131 | HP steam bypass spray drain | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 124/125/112/378/114/519/126/127 | IP FW to HP bypass FT iso | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | OPEN
VBFW 569/567 | IP FW to HP bypass vent | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 119/387 | IP FW to HP bypass drain before CV | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 513 | IP FW to HP bypass iso | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 557/551 | IP FW to HP bypass drain | Pipe Rack 3rd | Attemperator HP |  | BFW IP |  | CLOSED
VBFW 574/575 | HRH terminal attemperator before CV iso | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 576/577 | HRH terminal attemperator drain | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 124F/125F/126F/127F/100F/110F/104F/102F | HRH terminal atemperator flow meter (3 tramsmitters) | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 389/103 | HRH terminal drain after block valve (2) valves | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 118 | HRH terminal attemperator after CV iso | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 362/363 | HRH terminal drain after check valve (2) valves (3rd pipe rack) | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 618/619 | HRH terminal attemperator vent after check (3rd pipe rack) | Pipe Rack 2nd | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 918/919/820/821/822/823/824/825 | (2) Flow transmitters (8) valves | HRSG lower | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 960/961 | Drain before CV | HRSG lower | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 848/849 | Strainer Drain (2) valves | HRSG lower | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW 826/827/828/829 | Strainer DPT (4) valves | HRSG lower | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 930 | After CV iso | HRSG lower | Attemperator HRH |  | BFW IP |  | OPEN
VBFW 962/963 | Drain after check (2) valves | HRSG lower | Attemperator HRH |  | BFW IP |  | CLOSED
VBFW433/434 | CRH to AUX steam LOW flow attemperator ISO before CV | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW447/448 | Drain between attemperator isolation valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 431/432/156/157 | Flow transmitter (4) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 436/437 | Drain before CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 624/625 | Vent after CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 628/629 | Drain after CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 319 | CRH to AUX steam LOW flow attemperator ISO after CV | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 451/452 | Drain after check (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 570/571 | CRH to AUX steam HIGH flow attemperator ISO before CV | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 572/573 | Drain between attemperator isolation valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 140/141/142/143 | Flow transmitter (4) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 144/145 | Drain before CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 622/623 | Vent after CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 626/627 | Drain after CV (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 146 | CRH to AUX steam HIGH flow attemperator ISO after CV | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | OPEN
VBFW 454/453 | Drain after check (2) valves | Pipe Rack 3rd | Attempeator Aux |  | BFW IP |  | CLOSED
VBFW 113/390 | IP FW strainer #2 drain | Pipe Rack 1st | TCA |  | BFW IP |  | CLOSED
VBFW 162/163 | IP FW strainer #2 vent | Pipe Rack 1st | TCA |  | BFW IP |  | CLOSED
VBFW 296/297/298/299 | FW to TCA flow meter (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 300 | FW to TCA iso | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 301/302 | FW to TCA drain | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VBFW 303/304 | FW to TCA drain after CV | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VBFW 306 | From TCA iso | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 700/701/929/928 | PDI across TCA | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 307/308/309/310 | FW from TCA PITx2 (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 305/294 | Drain After TCA coller | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VBFW 311/312/313/314 | From TCA flow meter (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 315/316/317/318 | From TCA flow meter (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 324/325 | From TCA to HP economizer vent | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VBFW 320/321/326/327 | From TCA to HP economizer PDIT (4) valves | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 328/329 | From TCA to HP economizer drain after CV | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VHHS 948 | From TCA to HP economizer isolation | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VHHS 949 | From TCA to HP economizer isolation bypass | Pipe Rack 1st | TCA |  | BFW HP |  | CLOSED
VHHS 950 | From TCA to HP economizer isolation equalizing | Pipe Rack 1st | TCA |  | BFW HP |  | OPEN
VBFW 331/332 | From TCA to Cond. Receiver Tank vent | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 610/611 | From TCA to Cond. Receiver Tank drain | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 614/615 | From TCA to Cond. Receiver Tank vent (smr bldng) | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 330/922 | From TCA to Cond. Receiver Tank iso (2) vlvs | CRT | TCA |  | BFW HP |  | OPEN
VBFW 165/166 | From TCA to Cond. Receiver Tank drain | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 923/532 | From TCA to Cond. Receiver Tank strainer vent | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 333/334 | From TCA to Cond. Receiver Tank strainer drain | CRT | TCA |  | BFW HP |  | CLOSED
VBFW 322/323 | From TCA to Cond. Receiver Tank vent after srtainer | CRT | TCA |  | BFW HP |  | CLOSED
VBFW305/306 | From TCA to Cond. Receiver Tank drain after strainer | CRT | TCA |  | BFW HP |  | OPEN
VBFW | From TCA to Cond. Receiver Tank before CV iso | CRT | TCA |  | BFW HP |  | OPEN
VBFW339 | From TCA to Cond. Receiver Tank after CV iso | CRT | TCA |  | BFW HP |  | OPEN
VBFW | To Gas performance heater MOV bypass | one level under LP Drum | FGPH |  | BFW IP |  | CLOSED
VBFW461/462 | Drain berore startap heater | Pipe Rack 1st | FGPH |  | BFW IP |  | CLOSED
VBFW 120/121 | Startup heater drain | Pipe Rack 1st | FGPH |  | BFW IP |  | CLOSED
VBFW 117/110 | Startup heater vent | Pipe Rack 1st | FGPH |  | BFW IP |  | CLOSED
VBFW 578/579 | Vent after startap heater | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 340/341/342/343 | Gas performance heater flow | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 344 | Gas performance heater High flow CV iso (before) | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW345 | Gas performance heater High flow CV iso (after) | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW3346 | Gas performance heater Low flow CV iso (before) | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 347 | Gas performance heater Low flow CV iso (after) | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 285/348 | Gas performance heater nitrogen connection (after CV) | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 350/352 | Gas performance heater iso | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 351/286 | Gas performance heater drain | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 284/262 | Gas performance heater FW in PIT | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW357/274/356/273 | Gas performance heater Level switch vessel 1 | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW354/355/275/276 | Gas performance heater Level switch vessel 1 | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 153/353 | Gas performance heater Level switch vessel 1 vent | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 372/373/2278/279 | Gas performance heater Level switch vessel 2 | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 370/371/280/281 | Gas performance heater Level switch vessel 2 | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW369/277 | Gas performance heater Level switch vessel 2 vent | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 359/282 | Gas performance heater FW out PIT | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW 602/603 | Drain after Gas performance heater | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 616/617 | Gas performance heater drain | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 349/283 | Gas performance heater vent | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 289/360 | Gas performance heater drain before block valve | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW291/364 | Gas performance heater drain before CV | FGPH | FGPH |  | BFW IP |  | CLOSED
VBFW 367 | Gas performance heater outlet iso | FGPH | FGPH |  | BFW IP |  | OPEN
VBFW600/601 | Gas performance heater to receiver tank vent | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 290/361 | Gas performance heater to receiver tank iso (2) valves | CRT | FGPH |  | BFW IP |  | OPEN
VBFW 402/403 | Gas performance heater to receiver tank drain | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 440/441 | Gas performance heater to receiver tank strainer vent | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 292/366 | Gas performance heater to receiver tank strainer drain | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW449/450 | Gas performance heater to receiver tank after strainer drain | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 459/460 | Gas performance heater to receiver tank after strainer vent | CRT | FGPH |  | BFW IP |  | CLOSED
VBFW 379 | Gas performance heater to receiver tank iso after CV | CRT | FGPH |  | BFW IP |  | OPEN
VHLS 819/820/821/822/825/826/827/828 | LP steam flow transmitters | Pipe Rack 2nd | HRSG |  | HLS
VLPS 112/123 | LP steam header vents | Pipe Rack 2nd | HRSG |  | HLS
VHHS 818/819 | HP superheater outlet vent to atmoshpere (before MOV) | HRSG upper | HRSG |  | HHS
VHHS 998/999 | HP saturated steam sample (under HP drum) | HRSG upper | HRSG |  | HHS
VHHS 813/814/871/872/873/874 | HP superheater outlet PITs (before MOV) | HRSG upper | HRSG |  | HHS
VHHS 906 | 906 MOV bypass (HP steam isolation) | HRSG upper | HRSG/ST |  | HHS
VHHS 907 | 907 MOV bypass (HP steam isolation) | HRSG upper | HRSG/ST |  | HHS
VHPS 111/112 | HPS header vent | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 113/114/115/116 | HPS header PITs | Pipe Rack 3rd | HRSG/ST |  | HHS
VHHS 820/821/822/823/824/825/826/827 | HP steam FT before terminal attemperator | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 123/124/125/126/127/130 | HP steam FT after terminal attemperator | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 137/138 | HPS Bypass warmup line vent | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 828F/829F | HPS superheated steam sample isolation | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 128/129 | HPS Bypass vent | Pipe Rack 3rd | HRSG/ST |  | HHS
VHPS 119/120/121/122 | HPS Bypass PITs | Pipe Rack 3rd | HRSG/ST |  | HHS
VCRH 186/115 | CRH header vent | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 159/165 | CRH header vent | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 148/166 | CRH header PT | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 169/170/171/172/117/122/137/146 | CRH header Drip Leg Level Switches | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 174/124/147/173 | CRH header Drip Leg Level Switche drains | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH119/167/118/168 | CRH header Drip Leg Level Switche vents | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 111 | CRH header Drip Leg AOV iso | Pipe Rack 2nd | HRSG/ST |  | CRH
VCRH 136/185 | CRH header Drip Leg drain | Pipe Rack 2nd | HRSG/ST |  | CRH
VHRS 803/804 | CRH header PIT (HRSG) | HRSG upper | HRSG/ST |  | HRH
VHRS 909 | Nitrogen to CRH | HRSG upper | HRSG/ST |  | HRH
VHRS 807/808 | Nitrogen to CRH vent | HRSG upper | HRSG/ST |  | HRH
VHRS 969/970 | Reheater interstage Dripleg drain | HRSG upper | HRSG/ST |  | HRH
VHRS 903/904/911/912/813/814 | Reheater outet PITs | HRSG upper | HRSG/ST |  | HRH
VHRH 101/107 | HRH header vent | Pipe Rack 3rd | HRSG/ST |  | HRH
VHRH 135/136/187/188 | HRH header PIT (before attemperator) | Pipe Rack 3rd | HRSG/ST |  | HRH
VHRS 901/902 | HRH sample | Pipe Rack 3rd | HRSG/ST |  | HRH
VHRH 100/102/103/104/121/106 | HRH header PIT (after attemperator) | Pipe Rack 3rd | HRSG/ST |  | HRH
VHRH 108/109 | HRH header vent | Pipe Rack 3rd | HRSG/ST |  | HRH
VSTP 123 | GSC drain trap bypass | ST lower | ST seals |  | STP
VSTP 137 | GSC drain trap vent | ST lower | ST seals |  | STP |  | OPEN
VSTP 122 | GSC drain trap strainer drain | ST lower | ST seals |  | STP
VSTP 146/147/153/154 | GS Exhauster drains | ST lower | ST seals |  | STP
MAW01AA001 | GS Exhauster A inlet | ST upper West | ST seals |  | STP
MAW01AA002 | GS Exhauster B inlet | ST upper West | ST seals |  | STP
VSTP 125 | GS Exhauster A outlet | ST upper West | ST seals |  | STP
VSTP 179 | GS Exhauster B outlet | ST upper West | ST seals |  | STP
VAX 159 | GS supply iso before superheater | ST lower | ST seals |  | STP
VAXS 101 | GS supply vent before superheater | ST lower | ST seals |  | STP
VAXS 104/105 | GS superheater drain trap | ST lower | ST seals |  | STP
VAXS 107 | GS superheater drain trap bypass | ST lower | ST seals |  | STP
VAXS 106 | GS superheater drain trap strainer drain | ST lower | ST seals |  | STP
VAXS 196/197/198 | GS supply drain valves | ST lower | ST seals |  | STP
VSTP 148/149 | GS supply CV isolations | ST upper West | ST seals |  | STP
VSTP204 | GS supply CV bypass | ST upper West | ST seals |  | STP
VSTP 159/181 | GS mist separator orphis drain | ST lower | ST seals |  | STP
VSTP 167 | GS mist separator orphis bypass | ST lower | ST seals |  | STP
VSTP 182 | GS mist separator common drain | ST lower | ST seals |  | STP
VSTP 131/133 | GS header PT | ST lower | ST seals |  | STP
VSTP 183/184/185 | GS header drain | ST lower | ST seals |  | STP
VSTP 127/129 | GS spill over CV iso | ST lower | ST seals |  | STP
VSTP 132 | GS spill over CV bypass | ST lower | ST seals |  | STP
01-VAXS 171 | Steam to startup heater iso | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 109/110 | Startup Heater LIT isolation valves | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 121 | Steam to Startup Heater vent | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 124/125 | Drain from Startup Heater FC isolation valves | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 126 | Drain from Startup Heater line drain | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 127/156 | Drain from Startup Heater FC bypass | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VSMP 130F | Aux steam sample iso | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 187/188 | Aux steam header PITs | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 132 | Aux steam header vent (stmr bldg) | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS |  | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 200 | Drain before steam trap | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 117/201 | Steam trap iso | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 120 | Steam Trap bypass | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 119 | Steam Trap strainer drain | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 190 | Drain before steam trap | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 191/194 | Steam trap iso | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 202 | Steam Trap bypass | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VAXS 195 | Steam Trap strainer drain | Pipe Rack 1st | Aux Steam Header |  | AXS
01-VCRH 180/183 | CRH to Aux steam FC iso (Low flow) | Pipe Rack 3rd | Aux Steam Header |  | CRH
01-VCRH 181/184 | CRH to Aux steam FC iso (High flow) | Pipe Rack 3rd | Aux Steam Header |  | CRH
01-VCRH 120/162 | CRH to Aux steam vent | Pipe Rack 3rd | Aux Steam Header |  | CRH
01-VCRH 121/182 | CRH to Aux steam vent | Pipe Rack 3rd | Aux Steam Header |  | CRH
02-VAXS 189/290 | Steam to HP Evap Steam trap ISOs |  | Sparging
02-VAXS 289 | Steam to HP Evap Steam trap bypass |  | Sparging
02-VAXS 144 | Steam to HP Evap Steam trap strainer drain |  | Sparging
02-VAXS 291 | Steam to HP Evap drain before steam trap |  | Sparging
VHHS 904 | Steam to HP Evap MOV bypass |  | Sparging
VHHS 994/995 | Steam to HP Evap drain after MOV |  | Sparging
VHHS 996/997 | Steam to HP Evap strainer drain |  | Sparging
02-VAXS 133 | Steam to IP Evap vent | HRSG lower | Sparging |  | AXS
02-VHIS 909 | Steam to IP Evap MOV bypass | HRSG lower | Sparging |  | AXS
02-VHIS 860/861 | Steam to IP Evap drain after MOV | HRSG lower | Sparging |  | AXS
02-VHIS 852/853 | Steam to IP Evap strainer drain | HRSG lower | Sparging |  | AXS
02-VHLS 904 | Steam to LP Evap MOV bypass | HRSG lower | Sparging |  | AXS
02-VHLS 985/999 | Steam to LP Evap drain after MOV | HRSG lower | Sparging |  | AXS
02-VHLS 992/993 | Steam to LP Evap strainer drain | HRSG lower | Sparging |  | AXS
02-VAXS 135/136 | Steam to LP Evap Steam trap iso | HRSG lower | Sparging |  | AXS
02-VAXS 138 | Steam to LP Evap Steam trap bypass | HRSG lower | Sparging |  | AXS
02-VAXS 137 | Steam to LP Evap Steam trap strainer drain | HRSG lower | Sparging |  | AXS
02-VAXS 113 | Steam to LP Evap Drain before Steam trap | HRSG lower | Sparging |  | AXS
02-VAXS 155 | Drain before steam trap | HRSG lower West |  |  | AXS
02-VAXS 112/115 | Steam trap iso | HRSG lower West |  |  | AXS
02-VAXS 129 | Steam Trap bypass | HRSG lower West |  |  | AXS
02-VAXS 116 | Steam Trap strainer drain | HRSG lower West |  |  | AXS
02-VAXS 130 | Drain before steam trap | HRSG lower West |  |  | AXS
02-VAXS 103/161 | Steam trap iso | HRSG lower West |  |  | AXS
02-VAXS 164 | Steam Trap bypass | HRSG lower West |  |  | AXS
02-VAXS 160 | Steam Trap strainer drain | HRSG lower West |  |  | AXS
02-VAXS 292 | Aux steam header vent | HRSG lower West |  |  | AXS
00-VFGS220 | Emergency Shut Off Valve inlet isolation | GAS YARD | GAS YARD |  | FGS |  | Open
00-VFGS230 | Emergency Shut Off Valve inlet isolation | GAS YARD | GAS YARD |  | FGS |  | Open
00-VFGS221 | N2 Purge Isolation (fenced gas yard) | GAS YARD | GAS YARD |  | FGS |  | Closed
00-VFGS222 | N2 Purge Isolation (fenced gas yard) | GAS YARD | GAS YARD |  | FGS |  | Closed
00-VFGS803 | FILTER/SEPERATOR NITROGEN PURGE/VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS703 | FILTER/SEPERATOR NITROGEN PURGE/VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS719 | FILTER/SEPERATOR LEVEL CONTROL VALVE INLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS720 | FILTER/SEPERATOR LEVEL CONTROL VALVE OUTLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS722 | FILTER/SEPERATOR LEVEL CONTROL BYPASS |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS723 | FILTER/SEPERATOR LEVEL CONTROL VALVE INLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS724 | FILTER/SEPERATOR LEVEL CONTROL VALVE OUTLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS726 | FILTER/SEPERATOR LEVEL CONTROL BYPASS |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS819 | FILTER/SEPERATOR LEVEL CONTROL VALVE INLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS820 | FILTER/SEPERATOR LEVEL CONTROL VALVE OUTLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS822 | FILTER/SEPERATOR LEVEL CONTROL BYPASS |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS823 | FILTER/SEPERATOR LEVEL CONTROL VALVE INLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS824 | FILTER/SEPERATOR LEVEL CONTROL VALVE OUTLET |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS826 | FILTER/SEPERATOR LEVEL CONTROL BYPASS |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS705 | FILTER/SEPERATOR NITROGEN PURGE/VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS805 | FILTER/SEPERATOR NITROGEN PURGE/VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS708 | FILTER/SEPERATOR LEVEL COLUM SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS707 | FILTER/SEPERATOR LEVEL COLUM SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS711 | FILTER/SEPERATOR LEVEL GAGE SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS712 | FILTER/SEPERATOR LEVEL GAGE SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS708V | FILTER/SEPERATOR LEVEL GAGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS708D | FILTER/SEPERATOR LEVEL GAGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS704D | FILTER SEPERATOR COLUM DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS718 | FILTER/SEPERATOR LEVEL COLUM SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS717 | FILTER/SEPERATOR LEVEL COLUM SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS713 | FILTER/SEPERATOR LEVEL GAGE SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS714 | FILTER/SEPERATOR LEVEL GAGE SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS718V | FILTER/SEPERATOR LEVEL GAGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS718D | FILTER/SEPERATOR LEVEL GAGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS714D | FILTER SEPERATOR COLUM DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS709 | FILTER SEPERATOR LEVEL SWITCH ISOLATION LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS710 | FILTER SEPERATOR LEVEL SWITCH ISOLATION UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS715 | FILTER SEPERATOR LEVEL SWITCH ISOLATION LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS716 | FILTER SEPERATOR LEVEL SWITCH ISOLATION UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS704 | FILTER SEPERATOR DP TRANSMITTER HIGH SIDE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS706 | FILTER SEPERATOR DP TRANSMITTER LOW SIDE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS808 | FILTER/SEPERATOR LEVEL COLUM SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS807 | FILTER/SEPERATOR LEVEL COLUM SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS811 | FILTER/SEPERATOR LEVEL GAGE SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS812 | FILTER/SEPERATOR LEVEL GAGE SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS808V | FILTER/SEPERATOR LEVEL GAGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS808D | FILTER/SEPERATOR LEVEL GAGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS804D | FILTER SEPERATOR COLUM DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS818 | FILTER/SEPERATOR LEVEL COLUM SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS817 | FILTER/SEPERATOR LEVEL COLUM SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS813 | FILTER/SEPERATOR LEVEL GAGE SUPPLY LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS814 | FILTER/SEPERATOR LEVEL GAGE SUPPLY UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS818V | FILTER/SEPERATOR LEVEL GAGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS818D | FILTER/SEPERATOR LEVEL GAGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS814D | FILTER SEPERATOR COLUM DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS809 | FILTER SEPERATOR LEVEL SWITCH ISOLATION LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS810 | FILTER SEPERATOR LEVEL SWITCH ISOLATION UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS815 | FILTER SEPERATOR LEVEL SWITCH ISOLATION LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS816 | FILTER SEPERATOR LEVEL SWITCH ISOLATION UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS804 | FILTER SEPERATOR DP TRANSMITTER HIGH SIDE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS806 | FILTER SEPERATOR DP TRANSMITTER LOW SIDE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS731 | FILTER SEPERATOR DRAIN TANK DRAIN VALVE |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS727 | FILTER SEPERATOR DRAIN TANK LEVEL IND. TRANSMITTER LOWER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS728 | FILTER SEPERATOR DRAIN TANK LEVEL IND. TRANSMITTER UPPER |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS736 | FILTER SEPERATOR DRAIN TANK LEVEL TRASMITTER DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS729 | FILTER SEPERATOR DRAIN TANK LEVEL GAUGE DRAIN |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS730 | FILTER SEPERATOR DRAIN TANK LEVEL GAUGE VENT |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS732 | FILTER SEPERATOR DRAIN TANK LEVEL SWITH LOWER ISO. |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS735 | FILTER SEPERATOR DRAIN TANK LEVEL SWITH UPPER ISO. |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | OPEN
00-VFGS736 | FILTER SEPERATOR DRAIN TANK LEVEL SWITH DRAIN ISO. |  | FUEL GAS FILTER/SEPERATOR |  | FGS |  | CLOSED
00-VFGS733 | 12” FLOW METER STATION INLET |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS733D | 12” FLOW METER STATION INLET VALVE DRAIN |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS734 | 6” FLOW METER INLET |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS734D | 6” FLOW METER INLET VALVE DRAIN |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS744 | 6” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS748 | 6” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS747 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS743 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS737 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS739 | 12" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS741 | 12" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS745 | 12" YV-745 DRAIN VALVE |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS740 | 6" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS742 | 6" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (03) |  | FGS |  | OPEN
00-VFGS746 | 6" YV-746 DRAIN VALVE |  | FLOW METERING STATION (03) |  | FGS |  | CLOSED
00-VFGS833 | 12” FLOW METER STATION INLET |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS833D | 12” FLOW METER STATION INLET VALVE DRAIN |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS834 | 6” FLOW METER INLET |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS834D | 6” FLOW METER INLET VALVE DRAIN |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS844 | 6” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS848 | 6” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS847 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS843 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS837 | 12” FLOW METER NITROGEN PURGE/VENT |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS839 | 12" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS841 | 12" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (04) |  | FGS |  | P[EN
00-VFGS845 | 12" YV-845 DRAIN VALVE |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS840 | 6" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS842 | 6" PRESSURE TRANSMITTER ISOLATION |  | FLOW METERING STATION (04) |  | FGS |  | OPEN
00-VFGS846 | 6" YV-846 DRAIN VALVE |  | FLOW METERING STATION (04) |  | FGS |  | CLOSED
00-VFGS 229 | GAS SUPPLY ISOLATION TO HEATER |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS
00-VFGS245 | glycol supply to glycol heater |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | Open
00-VFGS246 | Glycol recirc pump skid isolation from fuel gas heat exchanger |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | Open
00-VFGS981 | GLYCOL FILL ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS984 | GLYCOL TANK SEPERATOR DRAIN VALV |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS976 | GLYCOL EXPANSION TANK ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS977 | GLYCOL EXPANSION TANK VENT |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS987 | GLYCOL EXPANSION TANK DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS968 | GLYCOL PUMP SUCTION TRANSMITTER ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS969 | GLYCOL PUMP SUCTION TRANSMITTER ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS968A | GLYCOL PUMP "A" SUCTION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS969A | GLYCOL PUMP "A" SUCTION STRAINER DP ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS970A | GLYCOL PUMP "A" SUCTION STRAINER DP ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS971A | GLYCOL PUMP "A" SUCTION STRAINER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS974A | GLYCOL PUMP "A" DISCHARGE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS973A | GLYCOL PUMP "A" DISCHARGE DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS972A | RECIRC ISOLATION PUMP "A" |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS968B | GLYCOL PUMP "B" SUCTION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS969B | GLYCOL PUMP "B" SUCTION STRAINER DP ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS970B | GLYCOL PUMP "B" SUCTION STRAINER DP ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS971B | GLYCOL PUMP "B" SUCTION STRAINER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS974B | GLYCOL PUMP "B" DISCHARGE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS973B | GLYCOL PUMP "B" DISCHARGE DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS972B | RECIRC ISOLATION PUMP "B" |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS974 | GLYCOL PUMPS DISCHARGE PRESSURE TRANSMITTER |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS975 | GLYCOL PUMPS DISCHARGE PRESSURE TRANSMITTER |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS983 | GLYCOL HEATER DP GUAGE HIGH SIDE ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS951 | GLYCOL HEATER DP GUAGE LOW SIDE ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS953 | GLYCOL HEATER DP DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS984 | GLYCOL HEATER DP DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS985 | GLYCOL HEATER GAS ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS986 | GLYCOL HEATER GAS STRAINER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS001 | GLYCOL HEATER GAS FLOW METER INLET VALVE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS002 | GLYCOL HEATER GAS FLOW METER INLET DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS021 | GLYCOL HEATER GAS PILOT ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS025 | GLYCOL HEATER PILOT HEADER DRAIN VALVE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS027 | GLYCOL HEATER PILOT HEADER DRAIN VALVE |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS028 | GLYCOL HEATER PILOT GAS TO BURNER ISOLATION |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS007 | GLYCOL HEATER MAIN GAS HEADER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS009 | GLYCOL HEATER MAIN GAS HEADER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS016 | GLYCOL HEATER MAIN GAS HEADER DRAIN |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | CLOSED
00-VFGS018 | GLYCOH HEATER MAIN GAS ISOLATION BEFORE BURNER |  | FUEL GAS DEW POINT HEATER/GLYCOL PUMP SKID |  | FGS |  | OPEN
00-VFGS755 | GLYCOL HEAT EXCHANGER NITROGEN PURGE/VENT (GAS SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS758 | GLYCOL HEAT EXCHANGER NITROGEN PURGE/VENT (GAS SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS855 | GLYCOL HEAT EXCHANGER NITROGEN PURGE/VENT (GAS SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS858 | GLYCOL HEAT EXCHANGER NITROGEN PURGE/VENT (GAS SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS959 | GLYCOL HEATER VENT (GLYCOL SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS958 | GLYCOL HEATER DRAIN (GLYCOL SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS965 | GLYCOL HEATER VENT (GLYCOL SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS964 | GLYCOL HEATER DRAIN (GLYCOL SIDE) |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS224 | glycol heat exchanger bypass/temperature control valve #1 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | THROTTLED
00-VFGS225 | glycol to fuel gas heat exchanger inlet #1 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | Open
00-VFGS226 | glycol from fuel gas heat exchanger outlet #1 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | Open
00-VFGS238 | glycol to fuel gas heat exchanger inlet #2 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS239 | glycol from fuel gas heat exchanger outlet #2 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS240 | glycol heat exchanger bypass/temperature control valve #2 |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS152 | GLYCOL HEAT EXCHANGER VENT |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS151 | GLYCOL HEAT EXCHANGER VENT |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS246 | GLYCOL RECIRC PUMP INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS245 | GLYCOL RECIRC PUMP OUTLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS150 | GLYCOL SUPPLY VENT/DRAIN |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | CLOSED
00-VFGS853 | PRESS TRANSMITTER ISOLATION #2 HEAT EXCHANGER INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS859 | PRESS TRANSMITTER ISOLATION #2 HEAT EXCHANGER INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS753 | PRESS TRANSMITTER ISOLATION #1 HEAT EXCHANGER INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS759 | PRESS TRANSMITTER ISOLATION #1 HEAT EXCHANGER INLET |  | GLYCOL HEAT EXCHANGER SKID |  | FGS |  | OPEN
00-VFGS200 | SKID08 HP reg station outlet to CT FUEAL GAS HEADER |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS782 | 6” OUTLET TO ELECTRIC HEATER NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS783 | 6” OUTLET TO ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS776 | 8” LOW FLOW REGULATING STATION INLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS776D | 8” LOW FLOW REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS782 | LOW FLOW NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS790 | LOW FLOW REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS793 | LOW FLOW REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS777 | 8” LOW FLOW REGULATING STATION INLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS777D | 8” LOW FLOW REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS794 | REDUCED GAS HEADER NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | Closed
00-VFGS774 | 16” SEC. REGULATING STATION INLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS774D | 16” SEC. REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS781 | SEC. REG. STATION NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS789 | SEC. REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS792 | SEC. REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS775 | 16” SEC. REGULATING STATION OUTLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS775D | 16” SEC. REGULATING STATION OUTLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS772 | 16” PRI. REGULATING STATION INLET |  | HP REGULATING STATION (08) |  | FGS |  | Open
00-VFGS772D | 16” PRI. REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS780 | PRI. REG. STATION NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | Closed
00-VFGS788 | PRI. REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS791 | PRI. REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS773 | 16” PRI. REGULATING STATION OULET |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS773D | 16” PRI. REGULATING STATION OULET DRAIN |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS783 | 6” OUTLET TO ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS253 | SKID08 HP reg. station outlet to fuel gas compressors |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS258 | N2 Purge Isolation |  | HP REGULATING STATION (08) |  | FGS |  | Closed
00-VFGS261 | GAS TO LP HEATER VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS262 | GAS TO LP HEATER VENT |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS263 | COMMON ISOLTION AFTER ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS260 | COMMON ISOLTION BEFORE ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS259/783? | LP GAS SUPPLY TO ELECTRIC HEATER |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS778 | COMMON REG STATION OULET PRESS TRANSMITTER ISO. VALVE |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS779 | COMMON REG STATION OULET PRESS TRANSMITTER ISO. VALVE |  | HP REGULATING STATION (08) |  | FGS |  | OPEN
00-VFGS788D | YV-788 DRAIN VALVE |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS785D | YV-785 DRAIN VALVE |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS787 | YV-787 DRAIN VALVE |  | HP REGULATING STATION (08) |  | FGS |  | CLOSED
00-VFGS210 | SKID09 hp reg station outlet bypass FG compressor |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS201/883?? | SKID09 HP REG STATION low pressure gas heater isolation |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS876 | 8” LOW FLOW REGULATING STATION INLET |  | HP REGULATING STATION (09) |  | FGS |  | Open
00-VFGS876D | 8” LOW FLOW REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS882 | LOW FLOW NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS890 | LOW FLOW REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS893 | LOW FLOW REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS877 | 8” LOW FLOW REGULATING STATION OUTLET |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS877D | 8” LOW FLOW REGULATING STATION OUTLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS894 | REDUCED GAS HEADER NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS874 | 16” SEC. REGULATING STATION INLET |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS874D | 16” SEC. REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS881 | SEC. REG. STATION NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS889 | SEC. REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS892 | SEC. REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS875 | 16” SEC. REGULATING STATION OUTLET |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS875D | 16” SEC. REGULATING STATION OUTLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS883?? | 6” OUTLET TO ELECTRIC HEATER |  | HP REGULATING STATION (09) |  | FGS |  | Open
00-VFGS872 | 16” PRI. REGULATING STATION INLET |  | HP REGULATING STATION (09) |  | FGS |  | Open
00-VFGS872D | 16” PRI. REGULATING STATION INLET DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS880 | PRI. REG. STATION NITROGEN PURGE/DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | Closed
00-VFGS888 | PRI. REG. STATION INNERSTAGE NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS891 | PRI. REG. STATION OUTLET NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS873 | 16” PRI. REGULATING STATION OULET |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS873D | 16” PRI. REGULATING STATION OULET DRAIN |  | HP REGULATING STATION (09) |  | FGS
00-VFGS257 | SKID09 HP reg. station outlet to fueal gas compressors |  | HP REGULATING STATION (09) |  | FGS |  | Open
00-VFGS254 | N2 Purge Isolation |  | HP REGULATING STATION (09) |  | FGS |  | Closed
00-VFGS257 | SKID 9 OUTLET TO GAS COMPRESSORS |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS884 | 6" TO ELECTIC HEATER NITROGEN PURGE/VENT |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS887D | YV-887 DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS878 | REGSTAION SKID 9 OUTLET PRESSURE TRANSMITTER |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS879 | REGSTAION SKID 9 OUTLET PRESSURE TRANSMITTER |  | HP REGULATING STATION (09) |  | FGS |  | OPEN
00-VFGS888D | YV-888 DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS885D | YV-885 DRAIN |  | HP REGULATING STATION (09) |  | FGS |  | CLOSED
00-VFGS901 | LP HEATER GAS NITROGEN PURGE/DRAIN VALVE |  | LP ELECTRIC HEATER |  | FGS |  | CLOSED
00-VFGS278 | Equipment Isolation (ANR/NB to chromatograph) |  | BOP GAS CHROMATOGRAPH |  | FGS |  | OPEN
00-VFGS279 | Equipment Isolation (Mix to chromatograph) |  | BOP GAS CHROMATOGRAPH |  | FGS |  | OPEN
00-VFGS280 | Equipment Isolation (Alliance to chromatograph) |  | BOP GAS CHROMATOGRAPH |  | FGS |  | OPEN
00-VFGS133 | GT Fuel Gas Calorie Meter Sample Tubing Isolation |  | GT FUEL GAS CALORIE METER |  | FGS |  | OPEN
00-VFGS136 | GT Fuel Gas Calorie Meter Sample Vent |  | GT FUEL GAS CALORIE METER |  | FGS |  | CLOSED
00-VFGS137 | GT Fuel Gas Calorie Meter Sample Tubing Isolation |  | GT FUEL GAS CALORIE METER |  | FGS |  | OPEN
00-VFGS202F | FG compressor “A” gas inlet |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS205F | FG compressor “A” gas outlet |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS281 | N2 Purge/vent Isolation (A compressor outlet) |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS476 | GAS COMPRESSOR “A” INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS442A | GAS COMPRESSOR “A” S/U PURGE INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS442B | GAS COMPRESSOR “A” S/U PURGE OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS442C | GAS COMPRESSOR “A” GAS PURGE NITROGEN FILL/DRAIN VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-446 | GAS COMPRESSOR “A” INLET HEADER DRAIN |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-448 | GAS COMPRESSOR “A” GAS SUPPLY TO SEAL FILTER |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-452 | GAS COMPRESSOR “A” DISCHARGE CONTROL VALVE BLEED |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-479 | GAS COMPRESSOR “A” OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-401A | GAS COMPRESSOR “A” SEAL SUPPLY FLOW VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-401B | GAS COMPRESSOR “A” SEAL SUPPLY BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-404 | NITROGEN SUPPLY TO SEAL BLOCK VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | Open
00-VFGS-424E | GAS COMPRESSOR “A” LUBE OIL FILTER PRESSURE EQUALIZATION VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-424A | GAS COMPRESSOR “A” 227A OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-424G | GAS COMPRESSOR “A” 227B OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-422 | GAS COMPRESSOR “A” CONTROL OIL TO VALVE 00-PSV-FGS-421 ISOLATION |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-423 | GAS COMPRESSOR “A” OIL RESERVOIR DRAIN |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-302 | FG Nitrogen Supply Isolation (A compressor) |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-449A | GAS COMPRESSOR "A" COMPRESSOR DISCHARGE PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-445A | GAS COMPRESSOR "A" COMPRESSOR INLET PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-450A | GAS COMPRESSOR "A" FLOW METER HIGH SIDE ISOLATION |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-450B | GAS COMPRESSOR "A" FLOW METER LOW SIDE ISOLATION |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-400A | GAS COMPRESSOR "A" SEAL GAS SUPPLY FILTER DP TRANSMITTER HIGH SIDE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-400B | GAS COMPRESSOR "A" SEAL GAS SUPPLY FILTER DP TRANSMITTER LOW SIDE |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-403A | GAS COMPRESSOR "A" SEAL VENT PRESSURE TRANSMITTER ISOLATION |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | OPEN
00-VFGS-149 | GAS COMPRESSOR "A" LUBE OIL SUPPLY DRAIN |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS-148 | GAS COMPRESSOR "A" LUBE OIL RETURN DRAIN |  | FUEL GAS COMPRESSOR "A" |  | FGS |  | CLOSED
00-VFGS203F | FG compressor “B” gas inlet |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
00-VFGS206F | FG compressor “B” gas outlet |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
00-VFGS-282 | N2 Purge/vent Isolation (B compressor outlet) |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” S/U PURGE INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” S/U PURGE OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” GAS PURGE NITROGEN FILL/DRAIN VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” INLET HEADER DRAIN |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” GAS SUPPLY TO SEAL FILTER |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” DISCHARGE CONTROL VALVE BLEED |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” SEAL SUPPLY FLOW VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” SEAL SUPPLY BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| NITROGEN SUPPLY TO SEAL BLOCK VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | Open
| GAS COMPRESSOR “B” LUBE OIL FILTER PRESSURE EQUALIZATION VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” 227A OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” 227B OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
| GAS COMPRESSOR “B” CONTROL OIL TO VALVE 00-PSV-FGS-421 ISOLATION |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR “B” OIL RESERVOIR DRAIN |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
00-VFGS-303 | FG Nitrogen Supply Isolation (A compressor) |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" COMPRESSOR DISCHARGE PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" COMPRESSOR INLET PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" FLOW METER HIGH SIDE ISOLATION |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" FLOW METER LOW SIDE ISOLATION |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" SEAL GAS SUPPLY FILTER DP TRANSMITTER HIGH SIDE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" SEAL GAS SUPPLY FILTER DP TRANSMITTER LOW SIDE |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
| GAS COMPRESSOR "B" SEAL VENT PRESSURE TRANSMITTER ISOLATION |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | OPEN
00-VFGS-147 | GAS COMPRESSOR "B" LUBE OIL SUPPLY DRAIN |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
00-VFGS-146 | GAS COMPRESSOR "B" LUBE OIL RETURN DRAIN |  | FUEL GAS COMPRESSOR "B" |  | FGS |  | CLOSED
00-VFGS204F | FG compressor “C” gas inlet |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
00-VFGS207F | FG compressor “C” gas outlet |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
00-VFGS283 | N2 Purge/vent Isolation (C compressor outlet) |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” S/U PURGE INLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” S/U PURGE OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” GAS PURGE NITROGEN FILL/DRAIN VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” INLET HEADER DRAIN |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” GAS SUPPLY TO SEAL FILTER |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” DISCHARGE CONTROL VALVE BLEED |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” OUTLET BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” SEAL SUPPLY FLOW VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” SEAL SUPPLY BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| NITROGEN SUPPLY TO SEAL BLOCK VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | Open
| GAS COMPRESSOR “C” LUBE OIL FILTER PRESSURE EQUALIZATION VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” 227A OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” 227B OIL FILTER VENT VALVE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
| GAS COMPRESSOR “C” CONTROL OIL TO VALVE 00-PSV-FGS-421 ISOLATION |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR “C” OIL RESERVOIR DRAIN |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
00-VFGS304 | FG Nitrogen Supply Isolation (A compressor) |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" COMPRESSOR DISCHARGE PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" COMPRESSOR INLET PRESSURE TRANSMITER |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" FLOW METER HIGH SIDE ISOLATION |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" FLOW METER LOW SIDE ISOLATION |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" SEAL GAS SUPPLY FILTER DP TRANSMITTER HIGH SIDE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" SEAL GAS SUPPLY FILTER DP TRANSMITTER LOW SIDE |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
| GAS COMPRESSOR "C" SEAL VENT PRESSURE TRANSMITTER ISOLATION |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | OPEN
00-VFGS-147 | GAS COMPRESSOR "C" LUBE OIL SUPPLY DRAIN |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
00-VFGS-146 | GAS COMPRESSOR "C" LUBE OIL RETURN DRAIN |  | FUEL GAS COMPRESSOR "C" |  | FGS |  | CLOSED
00-VFGS-800A | NITROGEN GENERATOR “A” INLET |  | NITROGEN GENERATOR |  | FGS |  | OPEN
00-FCV-FGS800A | NITROGEN GENERATOR “A” OUTLET FLOW CONTROL VALVE |  | NITROGEN GENERATOR |  | FGS |  | THROTTLED
00-VFGS-801A | NITROGEN GENERATOR “A” OUTLET BLOCK VALVE |  | NITROGEN GENERATOR |  | FGS |  | OPEN
00-VFGS-800B | NITROGEN GENERATOR “B” INLET |  | NITROGEN GENERATOR |  | FGS |  | OPEN
00-FCV-FGS-800B | NITROGEN GENERATOR “B” OUTLET FLOW CONTROL VALVE |  | NITROGEN GENERATOR |  | FGS |  | THROTTLED
00-VFGS-801B | NITROGEN GENERATOR “B” OUTLET BLOCK VALVE |  | NITROGEN GENERATOR |  | FGS |  | OPEN
00-VFGS301 | COMON GT GAS HEADER NITROGEN PURGE/VENT |  | COMMON GT HEADER |  | FGS |  | CLOSED
00-VFGS101 | COMON GT GAS HEADER PRESSURE TRANSMITTER ISOLATION |  | COMMON GT HEADER |  | FGS |  | OPEN
00-VFGS102 | COMON GT GAS HEADER PRESSURE TRANSMITTER ISOLATION |  | COMMON GT HEADER |  | FGS |  | OPEN
01-VFGS113 | UNIT 1 GAS FLOW METER INLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS124 | UNIT 1 GAS FLOW METER OUTLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS122 | UNIT 1 GAS FLOW METER BYPASS |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS116 | UNIT 1 GAS FLOW METER VENT |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA801 | UNIT 1 GAS FLOW METER PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA802 | UNIT 1 GAS FLOW METER PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS128 | UNIT 1 GAS PERFORMASE HEATER LT DRAIN VESSEL 1 |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA922 | UPPER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA924 | LOWER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA820 | UPPER TRANSMITTER ISOLATION 01MBP01CL121 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA821 | LOWER TRANSMITTER ISOLATION 01MBP01CL121 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA822 | UPPER TRANSMITTER ISOLATION 01MBPCL122 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA823 | LOWER TRANSMITTER ISOLATION 01MBPCL122 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS134 | UNIT 1 GAS PERFORMASE HEATER DRAIN LT VESSEL 2 |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA932 | UPPER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA934 | LOWER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA830 | UPPER TRANSMITTER ISOLATION 01MBP01CL131 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA831 | LOWER TRANSMITTER ISOLATION 01MBP01CL131 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA832 | UPPER TRANSMITTER ISOLATION 01MBPCL132 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA833 | LOWER TRANSMITTER ISOLATION 01MBPCL132 |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS130 | UNIT 1 FUEAL GAS PERFORMANCE HEATER ISOLATION TO AUTOMATIC VENT |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS123 | UNIT 1 BYPASS FUEL GAS PERFORMANCE HEATER VENT VALVE |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS115 | UNIT 1 FUEAL GAS PERFORMANCE HEATER NITROGEN PURGE/VENT |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS174 | UNIT 1 GT FUEL GAS FILTER INLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS192 | UNIT 1 GT FUEL GAS FILTER OUTLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS143 | UNIT 1 GT FUEL GAS FILTER NITROGEN SUPPLY |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS193 | UNIT 1 GT FUEL GAS FILTER INLET |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA907 | UNIT 1 FILTER DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA908 | UNIT 1 FILTER DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA911 | UNIT 1 FILTER DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA842 | UNIT 1 FILTER DP HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA843 | UNIT 1 FILTER DP HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA844 | UNIT 1 FILTER DP LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA845 | UNIT 1 FILTER DP LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP01AA909 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA910 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA912 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA907 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA908 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP01AA911 | UNIT 1 FILTER NITROGEN PURGE/DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS147 | PRESSURE TRANSMITTER 01MBP01CP110 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS148 | PRESSURE TRANSMITTER 01MBP01CP110 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS157 | PRESSURE TRANSMITTER 01MBP01CP111 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS158 | PRESSURE TRANSMITTER 01MBP01CP111 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01-VFGS177 | UNIT 1 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS178 | UNIT 1 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01-VFGS184 | UNIT 1 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP02AA807 | UNIT 1 GAS HEADER INLET PRESSURE TRANSMITTER 01MBP02CP141 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA808 | UNIT 1 GAS HEADER INLET PRESSURE TRANSMITTER 01MBP02CP141 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA801 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP101 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA802 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP101 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA803 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP102 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA804 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP102 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA805 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP103 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP02AA806 | UNIT 1 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP103 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA825 | UNIT 1 MAIN "A" DP TRANSMITTER 01MBP03CP521 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA826 | UNIT 1 MAIN "A" DP TRANSMITTER 01MBP03CP521 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA827 | UNIT 1 MAIN "A" DP TRANSMITTER 01MBP03CP521 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA828 | UNIT 1 MAIN "A" DP TRANSMITTER 01MBP03CP521 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA821 | UNIT 1 MAIN "A" PRESSURE TRANSMITTER 01MBP03CP136 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA822 | UNIT 1 MAIN "A" PRESSURE TRANSMITTER 01MBP03CP136 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA910 | UNIT 1 MAIN "A" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA911 | UNIT 1 MAIN "A" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA835 | UNIT 1 MAIN "B" DP TRANSMITTER 01MBP03CP531 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA836 | UNIT 1 MAIN "B" DP TRANSMITTER 01MBP03CP531 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA837 | UNIT 1 MAIN "B" DP TRANSMITTER 01MBP03CP531 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA838 | UNIT 1 MAIN "B" DP TRANSMITTER 01MBP03CP531 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA831 | UNIT 1 MAIN "B" PRESSURE TRANSMITTER 01MBP03CP146 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA832 | UNIT 1 MAIN "B" PRESSURE TRANSMITTER 01MBP03CP146 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA920 | UNIT 1 MAIN "B" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA921 | UNIT 1 MAIN "B" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA815 | UNIT 1 PILOT "A" DP TRANSMITTER 01MBP03CP501 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA816 | UNIT 1 PILOT "A" DP TRANSMITTER 01MBP03CP501 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA817 | UNIT 1 PILOT "A" DP TRANSMITTER 01MBP03CP501 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA818 | UNIT 1 PILOT "A" DP TRANSMITTER 01MBP03CP501 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA811 | UNIT 1 PILOT "A" PRESSURE TRANSMITTER 01MBP03CP126 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA812 | UNIT 1 PILOT "A" PRESSURE TRANSMITTER 01MBP03CP126 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA900 | UNIT 1 PILOT "A" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA901 | UNIT 1 PILOT "A" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA845 | UNIT 1 PILOT "B" DP TRANSMITTER 01MBP03CP511 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA846 | UNIT 1 PILOT "B" DP TRANSMITTER 01MBP03CP511 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA847 | UNIT 1 PILOT "B" DP TRANSMITTER 01MBP03CP511 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA848 | UNIT 1 PILOT "B" DP TRANSMITTER 01MBP03CP511 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA841 | UNIT 1 PILOT "B" PRESSURE TRANSMITTER 01MBP03CP156 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA842 | UNIT 1 PILOT "B" PRESSURE TRANSMITTER 01MBP03CP156 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA930 | UNIT 1 PILOT "B" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA931 | UNIT 1 PILOT "B" RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA855 | UNIT 1 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA856 | UNIT 1 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 HIGH SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA857 | UNIT 1 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA858 | UNIT 1 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 LOW SIDE ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA851 | UNIT 1 PILOT TOPHAT PRESSURE TRANSMITTER 01MBP03CP166 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA852 | UNIT 1 PILOT TOPHAT PRESSURE TRANSMITTER 01MBP03CP166 ISOLATION |  | UNIT 1 GT HEADER |  | FGS |  | OPEN
01MBP03AA940 | UNIT 1 PILOT TOPHAT RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
01MBP03AA941 | UNIT 1 PILOT TOPHAT RING DRAIN |  | UNIT 1 GT HEADER |  | FGS |  | CLOSED
02-VFGS113 | UNIT 2 GAS FLOW METER INLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS124 | UNIT 2 GAS FLOW METER OUTLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS122 | UNIT 2 GAS FLOW METER BYPASS |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS116 | UNIT 2 GAS FLOW METER VENT |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA801 | UNIT 2 GAS FLOW METER PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA802 | UNIT 2 GAS FLOW METER PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS128 | UNIT 2 GAS PERFORMASE HEATER LT DRAIN VESSEL 1 |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP02AA922 | UPPER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA924 | LOWER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA820 | UPPER TRANSMITTER ISOLATION 02MBP01CL121 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA821 | LOWER TRANSMITTER ISOLATION 02MBP01CL121 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA822 | UPPER TRANSMITTER ISOLATION 02MBP01CL122 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA823 | LOWER TRANSMITTER ISOLATION 02MBP01CL122 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS134 | UNIT 2 GAS PERFORMASE HEATER DRAIN LT VESSEL 2 |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP02AA932 | UPPER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA934 | LOWER ISOLTION FOR VESSEL LEVEL TRANSMITTER |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA830 | UPPER TRANSMITTER ISOLATION 02MBP01CL131 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA831 | LOWER TRANSMITTER ISOLATION 02MBP01CL131 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA832 | UPPER TRANSMITTER ISOLATION 02MBPCL132 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA833 | LOWER TRANSMITTER ISOLATION 02MBPCL132 |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS130 | UNIT 2 FUEAL GAS PERFORMANCE HEATER ISOLATION TO AUTOMATIC VENT |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS123 | UNIT 2 BYPASS FUEL GAS PERFORMANCE HEATER VENT VALVE |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS115 | UNIT 2 FUEAL GAS PERFORMANCE HEATER NITROGEN PURGE/VENT |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS174 | UNIT 2 GT FUEL GAS FILTER INLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS192 | UNIT 2 GT FUEL GAS FILTER OUTLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS143 | UNIT 2 GT FUEL GAS FILTER NITROGEN SUPPLY |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS193 | UNIT 2 GT FUEL GAS FILTER INLET |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA907 | UNIT 2 FILTER DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA908 | UNIT 2 FILTER DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA911 | UNIT 2 FILTER DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA842 | UNIT 2 FILTER DP HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA843 | UNIT 2 FILTER DP HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA844 | UNIT 2 FILTER DP LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA845 | UNIT 2 FILTER DP LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP01AA909 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA910 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA912 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA907 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA908 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP01AA911 | UNIT 2 FILTER NITROGEN PURGE/DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS147 | PRESSURE TRANSMITTER 02MBP01CP110 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS148 | PRESSURE TRANSMITTER 02MBP01CP110 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS157 | PRESSURE TRANSMITTER 02MBP01CP111 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS158 | PRESSURE TRANSMITTER 02MBP01CP111 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02-VFGS177 | UNIT 2 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS178 | UNIT 2 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02-VFGS184 | UNIT 2 GT DOWNSTREAM PURGE CREDIT VALVE NITROGEN PURGE/VENT |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP02AA807 | UNIT 2 GAS HEADER INLET PRESSURE TRANSMITTER 02MBP02CP141 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA808 | UNIT 2 GAS HEADER INLET PRESSURE TRANSMITTER 02MBP02CP141 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA801 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP101 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA802 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 01MBP02CP101 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA803 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 02MBP02CP102 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA804 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 02MBP02CP102 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA805 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 02MBP02CP103 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP02AA806 | UNIT 2 GAS SUPPLY PRESSURE TRANSMITTER 02MBP02CP103 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA825 | UNIT 2 MAIN "A" DP TRANSMITTER 02MBP03CP521 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA826 | UNIT 2 MAIN "A" DP TRANSMITTER 02MBP03CP521 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA827 | UNIT 2 MAIN "A" DP TRANSMITTER 02MBP03CP521 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA828 | UNIT 2 MAIN "A" DP TRANSMITTER 02MBP03CP521 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA821 | UNIT 2 MAIN "A" PRESSURE TRANSMITTER 02MBP03CP136 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA822 | UNIT 2 MAIN "A" PRESSURE TRANSMITTER 02MBP03CP136 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA910 | UNIT 2 MAIN "A" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA911 | UNIT 2 MAIN "A" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA835 | UNIT 2 MAIN "B" DP TRANSMITTER 02MBP03CP531 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA836 | UNIT 2 MAIN "B" DP TRANSMITTER 02MBP03CP531 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA837 | UNIT 2 MAIN "B" DP TRANSMITTER 02MBP03CP531 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA838 | UNIT 2 MAIN "B" DP TRANSMITTER 02MBP03CP531 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA831 | UNIT 2 MAIN "B" PRESSURE TRANSMITTER 02MBP03CP146 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA832 | UNIT 2 MAIN "B" PRESSURE TRANSMITTER 02MBP03CP146 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA920 | UNIT 2 MAIN "B" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA921 | UNIT 2 MAIN "B" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA815 | UNIT 2 PILOT "A" DP TRANSMITTER 02MBP03CP501 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA816 | UNIT 2 PILOT "A" DP TRANSMITTER 02MBP03CP501 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA817 | UNIT 2 PILOT "A" DP TRANSMITTER 02MBP03CP501 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA818 | UNIT 2 PILOT "A" DP TRANSMITTER 02MBP03CP501 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA811 | UNIT 2 PILOT "A" PRESSURE TRANSMITTER 02MBP03CP126 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA812 | UNIT 2 PILOT "A" PRESSURE TRANSMITTER 02MBP03CP126 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA900 | UNIT 2 PILOT "A" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA902 | UNIT 2 PILOT "A" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA845 | UNIT 2 PILOT "B" DP TRANSMITTER 02MBP03CP511 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA846 | UNIT 2 PILOT "B" DP TRANSMITTER 02MBP03CP511 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA847 | UNIT 2 PILOT "B" DP TRANSMITTER 02MBP03CP511 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA848 | UNIT 2 PILOT "B" DP TRANSMITTER 02MBP03CP511 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA841 | UNIT 2 PILOT "B" PRESSURE TRANSMITTER 02MBP03CP156 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA842 | UNIT 2 PILOT "B" PRESSURE TRANSMITTER 02MBP03CP156 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA930 | UNIT 2 PILOT "B" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA931 | UNIT 2 PILOT "B" RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA855 | UNIT 2 PILOT TOPHAT DP TRANSMITTER 01MBP03CP541 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA856 | UNIT 2 PILOT TOPHAT DP TRANSMITTER 02MBP03CP541 HIGH SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA857 | UNIT 2 PILOT TOPHAT DP TRANSMITTER 02MBP03CP541 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA858 | UNIT 2 PILOT TOPHAT DP TRANSMITTER 02MBP03CP541 LOW SIDE ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA851 | UNIT 2 PILOT TOPHAT PRESSURE TRANSMITTER 02MBP03CP166 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA852 | UNIT 2 PILOT TOPHAT PRESSURE TRANSMITTER 02MBP03CP166 ISOLATION |  | UNIT 2 GT HEADER |  | FGS |  | OPEN
02MBP03AA940 | UNIT 2 PILOT TOPHAT RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
02MBP03AA941 | UNIT 2 PILOT TOPHAT RING DRAIN |  | UNIT 2 GT HEADER |  | FGS |  | CLOSED
00-VFGS300 | Common header nitrogen purge/vent |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS227 | AUX BOILER REGULATION SKID ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS309 | AUX BOILER REG STATION VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS310 | BUILDING HEAT SUPPLY HEADER VENT BEFORE ISOLATOIN |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS264 | BUILDING HEAT GAS SUPPLY ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS311 | AUX BUILDING HEAT SUPPLY HEADER VENT BEFORE ISOLATOIN |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS265 | AUX BUILDING HEAT GAS SUPPLY ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS-YV-905 | DRAIN VALVE FOR YV-905 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS906 | AUX BOILER HEADER DRAIN BEFORE CONTROL VLV |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS908 | PRESSURE TRANSMITER ISOLATION INNERSTAGE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS909 | PRESSURE TRANSMITER ISOLATION INNERSTAGE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS915 | AUX BOILER INNERSTAGE PRESSURE REGULATION VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS911 | PRESSURE TRANSMITER ISOLATION AFTER REGULATION VALVE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS914 | PRESSURE TRANSMITER ISOLATION AFTER REGULATION VALVE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS312 | AUX BOILER HEADER NITROGEN PURGE/VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS228 | AUX BOILER GAS SUPPLY ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS917 | SUPPLY PRESSURE TRANSMITTER BUILDING HEAT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS913 | SUPPLY PRESSURE TRANSMITTER BUILDING HEAT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS904 | ORDERIZER RAW GAS SUPPLY ISOLATION TO ODORIZER PANEL |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGSXXX | ORDERIZER ORDERANT SUPPLY ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGSXXX | ORDERISER PANEL ORDERIZED GAS OUTLET |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGSXXX | ORDERIZER INJECTION POINT ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS912 | ORDERIZED GAS TO AUX BOILER BUILDING DRAIN BEFORE REGULATING VALVE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS920 | ORDERIZED GAS TO AUX BOILER BUILDING DRAIN INNERSTAGE REGULATING VALVE |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
01-VFGS244 | UNIT 1 TURBINE BUILDING GAS ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
02-VFGS241 | UNIT 2 TURBINE BUILDING GAS ISOLATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
01-VFGS941 | UNIT 1 TURBINE BUILING SUPPLY INTERSTAGE REGULATION VALVE VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
01-VFGS946 | UNIT 1 TURBINE BUILING HEAT REGULATION VALVE ISOLATION PCV-946 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
01-VFGS950 | UNIT 1 TURBINE BUILING HEAT REGULATION VALVE ISOLATION PCV-950 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS272 | UNIT 1 TURBINE BUILDING HEAT REGULATION SKID OUTLET |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS313 | UNIT 1 TURBINE BUILDING HEAT REGULATION SKID VENT BEFORE REGULATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS314 | UNIT 1 TURBINE BUILDING HEAT REGULATION SKID VENT AFTER REGULATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
02-VFGS941 | UNIT 2 TURBINE BUILING SUPPLY INTERSTAGE REGULATION VALVE VENT |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
02-VFGS946 | UNIT 2 TURBINE BUILING HEAT REGULATION VALVE ISOLATION PCV-946 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
02-VFGS950 | UNIT 2 TURBINE BUILING HEAT REGULATION VALVE ISOLATION PCV-950 |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS273 | UNIT 2 TURBINE BUILDING HEAT REGULATION SKID OUTLET |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | OPEN
00-VFGS315 | UNIT 2 TURBINE BUILDING HEAT REGULATION SKID VENT BEFORE REGULATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
00-VFGS316 | UNIT 2 TURBINE BUILDING HEAT REGULATION SKID VENT AFTER REGULATION |  | FG SUPPLY TO DUCT BURNERS/BUILDING HEATERS |  | FGS |  | CLOSED
01-VFGS176 | UNIT 1 DUCT BURNER REGULATION SKID ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS217 | UNIT 1 DUCT BURNER SKID VENT AFTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS-YV-922 | DRAIN ON STOP VALVE YV-922 |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-VFGS923 | UNIT 1 DUCT BURNER DRAIN BEFORE PRESSURE CONTROL VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-VFGS932 | UNIT 1 DUCT BURNER INTERSTAGE VENT |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-VFGS925 | UNIT 1 DUCT BURNER INNERSTAGE PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS926 | UNIT 1 DUCT BURNER INNERSTAGE PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS928 | UNIT 1 DUCT BURNER PRESSURE TRANSMITTER ISOLATION AFTER REGULATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS929 | UNIT 1 DUCT BURNER PRESSURE TRANSMITTER ISOLATION AFTER REGULATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS179 | UNIT 1 DUCT BURNER PRESSURE REGULATION OUTLET |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-VFGS120 | UNIT 1 DUCT BURNER SUPPLY VENT AFTER REGULATION SKID |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR800 | DUCT BURNER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR803 | GAS FLOW INDICATING TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR804 | GAS FLOW INDICATING TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR810 | PURGE ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR811 | PRESSURE INDCATING TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR812 | PRESSURE INDCATING TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR820 | PRESSURE INDICATION TRANSMITTER AFTER STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR845 | DRAIN AFTER STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR827 | DP TRANSMITTER HIGH SIDE STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR828 | DP TRANSMITTER LOW SIDE STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR846 | DUCT BURNER HEADER DRAIN |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR835 | PRESSURE AFTER CONTROL VALVE TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR836 | PRESSURE AFTER CONTROL VALVE TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-FG-V-0942 | DRAIN AFTER FLOW CONTROL VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR860 | PILOT GAS SUPPLY ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR866 | PILOT GAS PRESSURE TRANSMITTER ISOLATION |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR886 | PILIOT HEADER DRAIN BETWEEN PRIMARY STOP VALVES |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR870 | PILOT HEADER STOP VALVE PRESSURE DP HIGH SIDE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR871 | PILOT HEADER STOP VALVE PRESSURE DP LOW SIDE |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR887 | PILOT HEADER DRAIN BETWEEN STOP VALVES SECONDARY |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-FG-V-0943 | PILOT HEADER DRAIN AFTER LAST STOP VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
01-V-BUR955 | FLAME SCANNER BLOWER DISCHARGE PRESSURE TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BUR956 | FLAME SCANNER BLOWER DISCHARGE PRESSURE TRANSMITTER |  | UNIT 1 DUCT BURNER |  | FGS |  | OPEN
01-V-BURXXX | FLAME SCANNER BLOWER DISCHARGE DRAIN VALVE |  | UNIT 1 DUCT BURNER |  | FGS |  | CLOSED
02-VFGS176 | UNIT 2 DUCT BURNER REGULATION SKID ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS217 | UNIT 2 DUCT BURNER SKID VENT AFTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS-YV-922 | DRAIN ON STOP VALVE YV-922 |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-VFGS923 | UNIT 2 DUCT BURNER DRAIN BEFORE PRESSURE CONTROL VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-VFGS932 | UNIT 2 DUCT BURNER INTERSTAGE VENT |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-VFGS925 | UNIT 2 DUCT BURNER INNERSTAGE PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS926 | UNIT 2 DUCT BURNER INNERSTAGE PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS928 | UNIT 2 DUCT BURNER PRESSURE TRANSMITTER ISOLATION AFTER REGULATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS929 | UNIT 2 DUCT BURNER PRESSURE TRANSMITTER ISOLATION AFTER REGULATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS179 | UNIT 2 DUCT BURNER PRESSURE REGULATION OUTLET |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-VFGS120 | UNIT 2 DUCT BURNER SUPPLY VENT AFTER REGULATION SKID |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR800 | DUCT BURNER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR803 | GAS FLOW INDICATING TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR804 | GAS FLOW INDICATING TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR810 | PURGE ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR811 | PRESSURE INDCATING TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR812 | PRESSURE INDCATING TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR820 | PRESSURE INDICATION TRANSMITTER AFTER STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR845 | DRAIN AFTER STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR827 | DP TRANSMITTER HIGH SIDE STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR828 | DP TRANSMITTER LOW SIDE STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR846 | DUCT BURNER HEADER DRAIN |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR835 | PRESSURE AFTER CONTROL VALVE TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR836 | PRESSURE AFTER CONTROL VALVE TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-FG-V-0942 | DRAIN AFTER FLOW CONTROL VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR860 | PILOT GAS SUPPLY ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR866 | PILOT GAS PRESSURE TRANSMITTER ISOLATION |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR886 | PILIOT HEADER DRAIN BETWEEN PRIMARY STOP VALVES |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR870 | PILOT HEADER STOP VALVE PRESSURE DP HIGH SIDE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR871 | PILOT HEADER STOP VALVE PRESSURE DP LOW SIDE |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR887 | PILOT HEADER DRAIN BETWEEN STOP VALVES SECONDARY |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-FG-V-0943 | PILOT HEADER DRAIN AFTER LAST STOP VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED
02-V-BUR955 | FLAME SCANNER BLOWER DISCHARGE PRESSURE TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BUR956 | FLAME SCANNER BLOWER DISCHARGE PRESSURE TRANSMITTER |  | UNIT 2 DUCT BURNER |  | FGS |  | OPEN
02-V-BURXXX | FLAME SCANNER BLOWER DISCHARGE DRAIN VALVE |  | UNIT 2 DUCT BURNER |  | FGS |  | CLOSED